## BoardPublic
Suggested By | Date of Suggestion | Code Reference | Suggestion | Notes | Board Meeting Notes | Motion
Joe Williams | 2019-09-16 | 405.4 Approved designs, equipment and devices. | (1) The manufacturer, designer or engineer of the platform, car, cabin or chair safety device shall submit the design to the Elevator Safety Board and the Department. See Document B-1 | NEII COMMENT: Without any authority to enforce the acceptance of technology into the Commonwealth, there is no rationale for this information to be provided to the Board. The Department is the sole responsible party for issuing certificates of acceptance. | Board approved _ Dylan with NEII - Is this an expansion of the scope of what the statues call for,. | Approved
Joe Williams | 2019-09-17 | 405.4 Approved designs, equipment and devices. | (2) The Department will observe the operation and testing of the device for compliance with the Uniform Construction Code before [use of] the device is placed into service in this Commonwealth. See Document B-1 | NEII COMMENT: Without any authority to enforce the acceptance of technology into the Commonwealth, there is no rationale for this information to be provided to the Board. The Department is the sole responsible party for issuing certificates of acceptance. | Board Approved. Would like in Regs. | Approved
Joe Williams | 2019-09-18 | 405.4 Approved designs, equipment and devices. | (1) The Department will issue a certificate of acceptance after it observes successful testing of the device reports results of testing and observations to the Elevator Safety Board. See Document B-1 | NEII COMMENT: Without any authority to enforce the acceptance of technology into the Commonwealth, there is no rationale for this information to be provided to the Board. The Department is the sole responsible party for issuing certificates of acceptance. | Inspection, Joe feels we should have a report on the fails. | Approved
Joe Williams | 2019-09-18 | 405.5 Approved designs, equipment and devices. | The Department will conduct an acceptance inspection to confirm compliance with the Uniform Construction Code before a new elevator or lifting device or an elevator or lifting device under repair, alteration, or modification is put into service. All failed acceptance inspections shall be reported to the Elevator Safety Board, with a report and list of reasons for failure. See Document B-1 | NEII COMMENT: Statute allows the Board broad authority to make recommendations to the Secretary of Labor of Industry. However, the lawmakers of Pennsylvania were purposeful and clear about the information that is required to be shared with Board pursuant to their duties. Other than information related to variance requests, where statute is clear, the Commonwealth’s legislators specifically did not empower the Board with any additional enforcement capabilities or the authority to collect additional information from elevator companies, building owners and/or private citizens. Compliance, accident and product information is sensitive in nature and can be misinterpreted, misused or mishandled - especially without quality control measures in place. There is no reason for this information to be provided to the Board on a routine basis. If the Board needs additional information specific to a variance request or such details are deemed necessary to carry out its general functions, the Department can provide a characterization of issues in aggregate without company-specific details. Requiring the additional information as proposed in 405.5, 405.6, 405.10 and 405.11 will not make the Board more successful in carrying out its duties but has the potential to lead to unintended consequences. | Public comment - is this an expansion of board duties. Mr. Simns said the inspections cause delays and money for building owners. | Approved
Joe Williams | 2019-09-18 | § 405.8. Periodic testing. | (1) Category One under section 8.11.2.2 at 12 month intervals See Document B-1 | NEII COMMENT: NEII supports the proposed intervals for periodic testing outlined under 405.8 as they are in alignment with what is recommended by ASME A17.1/CSA B44 (“A17.1/B44”). However, the A17.1/B44 does not require weight tests every five years. Alternative testing is allowed by A17.1/B44 and there is no justification for restricting it arbitrarily. In fact, alternate testing eliminates the need for elevator mechanics to physically transport thousands of pounds of test weights in and out of buildings. Alternate testing is based on physics and has the potential to reduce strains and sprains, which are among the most common injuries for elevator workers. |  | Susan would like to include the next five lines. All approved. In yellow Motion was voted and approved.
Joe Williams | 2019-09-18 | § 405.8. Periodic testing. | (2) Category Five under section 8.11.2.3 at 5-year intervals. With weights and at contract speed. See Document B-1 | See Comment above | The question would be where to include in the regs. Joe W suggests leaving it here. | Approved
Joe Williams | 2019-09-18 | § 405.8. Periodic testing. | (3) Category One under section 8.11.3.2 at 12 month intervals. [Periodic inspection and testing shall be phased in over a 3-year period as following | See Comment above |  | Approved
Joe Williams | 2019-09-18 | § 405.8. Periodic testing. | (5) Category Five under section 8.11.3.4 at 5-year intervals with weights and at contract speed. See Document B-1 | See Comment above | Approved should be considered for alternate testing as well. That is we added with weights. Have to do 3 & 5 with weights. | Approved
Joe Williams | 2019-09-18 | § 405.8. Periodic testing. | (6) Category One under section 8.11.4.2 at 12 month intervals | See Comment above |  | Approved
Joe Williams | 2019-09-18 | § 405.10. Major repairs, replacements and alterations. | (c) An elevator or lifting device shall be taken out of service when a major repair, replacement or alteration is performed upon it. The owner or owner’s agent shall provide written notification to the Elevator Safety Board and the Department when the major repair, replacement or alteration is completed. The elevator or lifting device [may] shall not be returned to service [when it passes a Department inspection] until the Department conducts an inspection and passes the elevator or lifting device. All failed inspections shall be reported to the Elevator Safety Board with a report of failures and list of reasons for failure. See Document B-1 | NEII COMMENT: Without any authority to inspect equipment, there is no rationale for this information to be provided to the Board. The Department is the sole responsible party for inspecting an elevator or lifting device before it can be returned to service. |  | Motion caries.
Joe Williams | 2019-09-18 | § 405.11. Accident report. | (a) An owner of an elevator or lifting device or an authorized agent shall submit an accident report to the Elevator Safety Board and the Department if the elevator or lifting device is involved in an accident resulting in any of the following: See Document B-1 | NEII COMMENT: Statute does not permit the Board to expand its authority to determine when equipment can return to operation. The proposed changes to 405.11 directly conflict with law. Since the Board has no authority to inspect and determine if equipment can return to operation, there is no reason for accident and/or inspection information to be provided to the Board. |  | Approved
Joe Williams | 2019-09-18 | § 405.11. Accident report. | (b) The owner or authorized representative shall submit the accident report on a Department-prescribed form, which must be received by the Elevator Safety Board and the Department within 24 hours of the accident. See Document B-1 | See above comment
Joe Williams | 2019-09-18 | § 405.11. Accident report. | An elevator or lifting device that was involved in a fatal accident may not return to operation until the Elevator Safety Board and the Department provides approval. See Document B-1 | See above comment
Joe Williams | 9/172019 |  | Elevator Personnel: Persons who have been trained in the construction, maintenance, repair testing of equipment and are enrolled in or have completed a certified elevator apprenticeship program approved by the Commonwealth of Pennsylvania. Personnel whom have been established as elevator personnel prior to the effective date of this statute as defined by being awarded completion of a nationally recognized elevator education program approved by the Commonwealth of Pennsylvania and have at least 5 years unsupervised experience working in the elevator industry shall be considered elevator personnel. | Rationale: A national standard does not provide the details of what training is as it is not an enforcing entity, while a jurisdiction as an enforcing entity and adopting the standard as their code defines the training so as to ensure qualified personnel are in place to perform work in these areas. NEII COMMENT appreciates the need for licensing requirements and will work towards implementing the Model Elevator Law in PA. Elevators are complex pieces of equipment and those that work on them should meet a baseline level of training and on-the-job hours. However, this change goes beyond the scope of the code update and should be addressed in a separate legislative process. ASME has carefully considered this term and its associated definition, which should not be modified. Elevator personnel can include other people who are trained on the construction, maintenance, repair, inspection, or testing of equipment (i.e., inspectors). | Joe W, anyone can run a car at this point. Some folks do not know what they are doing. We would like trained personnel. (Defined) Define as well who should be going into the hatch. Persons that have been training in inspections. Add qualified inspection program - (Last sentence change and to or) We would have to define elevator personnel) Five years experience, 2 recognized inspection program and are in an apprentice program under the tutelage or completed an apprentice program. A - 17 says qualified Elevator personnel At this point they just want language to limit who runs construction elevator. | Definition Approved by Motion: Joe will rewrite this one and come back. Elevator Personnel: Persons who have been trained in the construction, maintenance, repair, testing of equipment and are enrolled in or have completed a certified elevator apprenticeship program approved by the Commonwealth of Pennsylvania. Persons who have passed the Qualified Elevator Inspector exam. Persons who have been established as elevator personnel prior to the effective date of this statue as defined by being awarded completion of a nationally recognized elevator education program approved by the commonwealth of Pennsylvania and have at least 5 years of unsupervised experience working in the elevator industry shall be considered elevator personnel.
Dave Wade | 2019-09-17 | Part IV Hydraulic Elevators | Board would like to include in Regulation package. Single Bottom Jacks issue. See Document B-2 |  |  | Motion voted on and approved - No single bottom jacks in PA 8.658 has language on this but we to phase them out. Previous motion was approved on the issue. Prevoius motion was three years.
| 2019-09-18 | Hoistway Door, Toe Plates, car Door restrictors, Fire Service Keys (phase 1 & 2), Power Shut_off Location for MRLs, Car size EMS Use, Inspections on Fire Service Controls Phase 1 & 2, Fire Service Awareness / Operations Training (online?) | See Documents B-3 & B-4 |  |  | Will revisit
Dylan Isenberg NEII | 2019-10-17 | Comments on changes to the standards. | General Statement: All provisions in ASME A17.1/B44 are thoroughly vetted through a consensus process. This process functions by committees comprised of experts from all industry interest groups including enforcing authorities, engineers, building owners and organized labor. Committees use Hazard Assessments to evaluate potential safety risks for changes. Because of this rigorous, consensus process, local changes to the model code are not recommended unless dictated by conditions completely unique to a jurisdiction such as extreme weather, seismic, etc. Additionally, the ASME code is developed to harmonize with the other codes (fire, building, electrical, etc.). Conflicts, and potential safety issues, are created when the elevator code is amended without consideration of other codes. | Comments in relation to other comments previously submitted. See Document E_6_NEII_PA-Comments_Elevator_Code | Dylan had no additional comments today. | No Motion needed.
Joe Williams | 2019-10-17 | 401.1Definitions. | Joe Williams suggested the following: Elevator personnel: Persons who are enrolled in or have completed a certified apprentice program approved by the Commonwealth of Pennsylvania. | Comments in relation to other comments previously submitted. See Document E_6_NEII_PA-Comments_Elevator_Code NEII Comment: NEII appreciates the need for licensing requirements and will work towards implementing the Model Elevator Law in PA. Elevators are complex pieces of equipment and those that work on them should meet a baseline level of training and on-the-job hours. However, this change goes beyond the scope of the code update and should be addressed in a separate legislative process. ASME has carefully considered this term and its associated definition, which should not be modified. Elevator personnel can include other people who are trained on the construction, maintenance, repair, inspection, or testing of equipment (i.e., inspectors).
Joe Williams | 2019-10-17 | Part 2 (Electric Elevators) | 2.4.2.4.2 remove language permitting retractable ladders. Retractable ladders lead to less clearance in shaft, increasing the risk of caught between, struck by hazards. | Comments in relation to other comments previously submitted. See Document E_6_NEII_PA-Comments_Elevator_Code NEII COMMENT: NEII believes this is supposed to be in reference to 2.2.4.2, which is the section that addresses the use of ladders. The same clearance requirements apply to both fixed and retractable ladders. Retractable ladders that may be in line of travel are required to have an electrical device to remove power from the motor and brake when it is not in the retracted position. Since this device prevents car movement, A17.1 mitigates the potential of getting struck by hazards. In many situations retractable ladders reduce the reach risk and fall hazard for elevator personnel and inspectors when accessing the pit from the landing. Use of this type of ladder has shown safety benefits in its installations. | Joe, has no problem with retractable ladders. He agrees with this language. | Motion carries Accept NEII recommendation.
Joe Williams | 2019-10-17 | 2.7.5.4 remove Why would we allow a working platform to be installed in the line of movement of the car or counterweight? | Why would we allow a working platform to be installed in the line of movement of the car or counterweight? | See Document E_6_NEII_PA-Comments_Elevator_Code NEII COMMENT: Working platforms are used to provide safe and convenient access to components in the hoistway that require inspection, maintenance, repair and replacement. ASME requires retractable stops and a means to prevent vertical car movement as a way to mitigate hazards from moving equipment. | Joe W, we my need additional information on this. Should not allow equipment that needs working platform. Joe (BOIS) the standard places additional safety features in place. Travel stops etc.… SIMS were they tested at contract speed, Joe said no. The video was a simulation. Joe M the platform is provided for additional safety. Do we need to add that these would be tested every six months. This is part of the code. | Motion to approved was voted and approved. To accept NEIIs recommendation. NEII stated that they have none in operation in the US.
Joe Williams | 2019-10-17 | 2.7.6.3.2(e) and (f) AGP | 2.7.6.3.2(e) and (f) AGP, accessible to general public is not defined in the standards definitions. AGP needs to be clearly defined. A sign inside the controller door is not effective. In an area that the code is stating is accessible to the general public the sign needs to be placed in a position that the general public can see and understand. Replace the language pertaining to the sign to read: shall be prominently posted on the outside of the of motor controller closet/room door indicating in letters not less than 25mm (lin) high, CAUTION ENSURE AREA IS SECURED AND SAFE BEFORE OPENING | See Document E_6_NEII_PA-Comments_Elevator_Code NEII COMMENT: The term “Accessible to the General Public” is spelled out in the notes to Requirement 2.26.4.2. In addition, the controller door is required to be opened only with a Group 1 security key, meaning it can only be unlocked by elevator personnel who are trained. Therefore, additional signage is unnecessary because elevator personnel should already be familiar with how to safely access control systems. | Joe W, this is why we asked for a better definition of elevator personnel. Joe W is asking for a sign on the door on inside and outside to ensure the area is secure. . Now you could be working in a public space. (hallway) Public - the comment was in relation to a sign in a controlled public space. AGP - Typically they do mark it but not required by code. The AGP is for a piece of equipment in a public area. Joe M said the code says it needs to be on the inside and not outside. You can have impact on accessibility issues. Joe M - you are putting a bulls eye on the elevator equipment with a sign. | Joe W is to add sinage language to 2,7.3 AGP needs to be clearly defined, posted on outsdie of controler. Motion Carried.
Joe Williams | 2019-10-17 | 2.12.7.2.1 remove (c) | 2.12.7.2.1 remove (c) installing an access switch on a sight guard is creating more struck by, caught between and electrocution hazards by moving personnel closer to moving parts. | See Document E_6_NEII_PA-Comments_Elevator_Code NEII COMMENT: In order to improve safety, changes were made to this requirement in the 2016 edition of A17.1 limiting where an access switch could be located. The sight guard is outside the line of movement of the elevator and therefore should not create any new hazards. | Do not think it is safe to put on sight guard. . | Motion for this one and the one below to limit not on sightguard. 2.12.2.1 and the next one below. Motion Carries
Joe Williams | 2019-10-17 | 2.12.7.2.2 remove along with c from 2.12.7.2.1 | 2.12.7.2.2 remove along with c from 2.12.7.2.1 | See Document E_6_NEII_PA-Comments_Elevator_Code NEII COMMENT: This needs to be retained along with the previous requirement to ensure the sight guard is adequate to support the access switch. |  | Same Motion Carries
Joe Williams | 2019-10-17 | 2.12.7.3.3 (c) | 2.12.7.3.3 (c) remove the part of the sentence "unless the travel of the car limits such movement" why would we allow a lowered safety condition than the range permitted 84"- 96". | See Document E_6_NEII_PA-Comments_Elevator_Code NEII COMMENT: In some cases, the total travel of the elevator is less than 84 inches. Since the access switch cannot move the elevator beyond the distance it is able to travel, the exception is needed for these limited applications. | They could come to the board for limited access. "unless the travel of the car limits such movement" | They need to get a variance in this situation.
Joe Williams | 2019-10-17 | 2.27.3.1.6 © | 2.27.3.1.6 (c) remove. Why do they want stop switch to be operative during FIRE RECALL operation? | See Document E_6_NEII_PA-Comments_Elevator_Code NEII COMMENT: In-car stop switches are required to be a Group 1 key so that they are only available to elevator personnel who are trained properly. Emergency stop switches are allowed only in freight elevators with a trained operator. Elevator personnel and trained operators are able to evaluate the situation based on their training and should retain access to the stop switch during Phase I to allow them to control the movement of the car and prevent it from moving toward a hazard. | 2016 code allows to make the stop switch operable. If keyed stop switch behind panel they want trained responders to have the ability to control the car. Jow W to have a stop switch in place that could be overwritten is not advisable. (This relates to definition of authorized elevator personnel) | Motion made to make the stop switch inoperaple phase 1. Motion carried 4-3
Joe Williams | 2019-10-17 | Part 5 (Special application elevators) 5.10 | Part 5 (Special application elevators) 5.10 Add following sentence to the end 5.10; Elevators used for construction shall only be operated by elevator personnel, meeting the definition listed in the this standard 401.1 or by persons who have completed or enrolled in an approved operating engineer apprenticeship. | See Document E_6_NEII_PA-Comments_Elevator_Code NEII COMMENT: See comments related to definition of elevator personnel regarding the scope of the code update. Additionally, this is not the standard practice in jurisdictions. | Dylan - stated this creates a lot of issues with meeting the requirements. | Joe to rewrite personnel description. Tabled
Joe Williams | 2019-10-17 | Part 3 (Hydraulic Elevators) 6.1.7.4.3 and 6.2.7.4.3 | Part 3 (Hydraulic Elevators) 6.1.7.4.3 and 6.2.7.4.3 There is a concern over referencing non safety standards, ISO is not a safety organization. We need to guard the safety circuits so that a device cannot be activated within 200 mm of the circuit. | See Document E_6_NEII_PA-Comments_Elevator_Code NEII COMMENT: A17.1/B44 was updated to reference the ISO Standard, which is an international standard for safety requirements relative to electromagnetic interference instead of the previous European standard. This standard is recognized internationally and no justification is provided as to why this provision is of concern or should be modified/removed as opposed to the single requirement currently in A17.1/B44. | Joe W asking to guard circuits with 200 mm so they cannot activated. Bruce: the standard tests for all frequencies. EN standards are no longer recognized. ISO standards are recognized. | We have a motion table - table this one for additional infromation.
Joe Williams | 2019-10-17 | Part 7 (Dumbwaiters and material lifts) | Part 7 (Dumbwaiters and material lifts) 7.1.7.10 refers to 2.7.6.3.2 so the signage should be same as recommended above. | See Document E_6_NEII_PA-Comments_Elevator_Code NEII COMMENT: See comments for 2.7.6.3.2 | This one is redundant. | No need for discussion - redundent
Joe Williams | 2019-10-17 | Part 8 (General requirements) 8.6.1.2.2 | Part 8 (General requirements) 8.6.1.2.2 The following language was deleted from A17.1-2016 but was not supposed to be. It is in the A17.1-2010 edition as: "Where a defective elevator part directly affecting the safety of the operation is identified, the equipment shall be taken out service until the defective part has been adjusted, repaired, or replaced." This needs to be added to the PA edition. | See Document E_6_NEII_PA-Comments_Elevator_Code NEII COMMENT: We support this recommendation as long as it is added as 8.6.1.2.3 and not as part of 8.6.1.2.2. |  | Motion made and seconded to support the language on the left. Motion carries 8.6.1.2.3
Joe Williams | 2019-10-17 | 8.6.11.10 | 8.6.11.10 Remove this and all of it's sub parts to avoid any confusion over alternative testing. | See Document E_6_NEII_PA-Comments_Elevator_Code NEII COMMENT: No rationale is provided for a proposal disallowing alternative testing in PA. Alternative testing was added in the 2013 edition of ASME after passing a rigorous, consensus process. The code recognizes that certain technology exists to perform tests without the need for elevator personnel to move heavy test weights, thereby reducing the likelihood of injury to elevator personnel. Strains and sprains, which are often the direct result of moving weights for these tests, account for over half of all injuries to elevator personnel. Additionally, the Department retains the ability to authorize any alternative testing before its implemented in the Commonwealth. | Table for additional comments | Tabled to later - alternative testing discussion - 8.6.11.10 Put on calendar.
Joe Williams | 2019-10-17 | Remove the following; 8.6.11.10.1, 8.10.22.2 8.6.1.7.2 8.6.4.19.12 8.6.4.20.4 8.6.11.20.10, 8.6.11.10.2 8.6.11.10.3 8.6.11.10.4 | Remove the following; 8.6.11.10.1, 8.10.22.2 8.6.1.7.2 8.6.4.19.12 8.6.4.20.4 8.6.11.20.10, 8.6.11.10.2 8.6.11.10.3 8.6.11.10.4 | See Document E_6_NEII_PA-Comments_Elevator_Code NEII COMMENT: Removing these complete sections, which all make some reference to alternate testing, also eliminates important elements of code that are required for standard testing, too. First, some of the other sections listed above do not even exist. Second, removing these whole sections creates numerous safety hazards not the least of which is eliminating requirements for critical safety tests and inspections. Finally, requirement 8.6.11.10.1 allows alternative testing “subject to the authority having jurisdiction”. Since the AHJ has the final say anyway, there is no need to strike the language in these sections that deals with alternative testing. Striking these sections entirely is a safety regression, not enhancement. | Table for additional comments | Tabled
Joe Williams | 2019-10-17 | 8.6.11.15 | 8.6.11.15 Delete. How can elevator personnel maintain something when they are not present? | See Document E_6_NEII_PA-Comments_Elevator_Code NEII COMMENT: The requirement is needed to ensure that elevator personnel close and lock the cabinet prior to leaving the work area. The Group 1 security keys are limited to elevator personnel, so the provision ensures that the cabinet remains locked while they are away. See also previous comments on 2.7.6.3.2 | Need a better definition for elevator personnel. The concern is also that if someone is away for months they are responsible. The department says the intent of this is the person leaving must lock when leaving the area. This is the department ts take. NEII wants to work with the board on licensing requirements.
Joe Williams | 2019-10-17 | 8.7.2.14.5.2 | 8.7.2.14.5.2 Delete. Collapsible railings lower the minimum safety standard. Introducing struck by and caught between hazards. | See Document E_6_NEII_PA-Comments_Elevator_Code NEII COMMENT: These railings are only allowed on existing equipment where full compliance with 2.14.1.7 is not possible. Having a collapsible railing is preferred to no railing at all on some older equipment. The code requires the railing to be in place before elevator personnel can operate the equipment and ride the car top in inspection mode. Therefore, it provides equivalent safety to a fixed railing when it is deployed. | Joe, if someone needs a collapsible railing they should get a variance. Public comments suggests adding language to include when it is being used. | OK to not change this area. Motion to remove orrogional suggestion and and observe the language in code. Motion carries.
Dylan Isenberg NEII | 2019-10-17 | § 405.2. Standards. | NEII SUGGESTS MAKING THE FOLLOWING LANGUAGE CHANGES TO THE LANGUAGE IN THE PROPOSED REGULATIONS from 10.17.19 (a) The following standards are adopted as part of the Uniform Construction Code and apply to the listed type of elevator or other lifting device. Other authorities referenced in the standards are adopted if the authority is not excluded in subsection (b): (1) [‘‘ASME A17.1-2000’’ with ‘‘A17.1a-2002’’ addenda] “ASME A17.1-2016”: ADD THE FOLLOWING LANGUAGE: Safety Code for Elevators and Escalators: (i) Part 1 (General). (ii) Part 2 (Electric elevators). (iii) Part 3 (Hydraulic elevators). (iv) Part 4 (Elevators with other types of driving machines). (v) Part 5 (Special application elevators). (vi) Part 6 (Escalators and moving walks). (vii) Part 7 (Dumbwaiters and material lifts). (viii) Part 8 (General requirements). (ix) Part 9 (Standard codes and specifications). ADD THE FOLLOWING LANGUAGE: (2) (2) ASME A17.3-2017: Safety Code for Existing Elevators and Escalators ADD AND REMOVE THE FOLLOWING LANGUAGE: (3) ["ASME B20.1-2000"] "ASME B20.l-2018" REMOVE THE FOLLOWING LANGUAGE: for Vertical and Inclined Reciprocating Conveyors without automatic transfer devices. ADD THE FOLLOWING LANGUAGE: Safety Standard for Conveyors and Related Equipment. ADD AND REMOVE THE FOLLOWING LANGUAGE: NOTE - #3 now becomes #4 (4) [''ASMEA90.l-1997'' including ''A90.la-1999'' and ''A90.lb-2001'' Addenda] "ASME A90.l-2015" ADD THE FOLLOWING LANGUAGE: Safety Standards for Belt Man-lifts.(4) ["ANSI B77.l-2011" and supplement "ANSI B77.la-2012"] "ANSI B77.l-2017'' for Passenger Ropeways-Aerial Tramways, Aerial Lifts, Surface Lifts, Tows and Conveyors ADD THE FOLLOWING LANGUAGE: Safety Standard. (5) ["ASME A18.l-1999" including "A.18.la-2001" addenda] "ASME A18.1 2017" ADD THE FOLLOWING LANGUAGE: Safety Standard for Platform Lifts and Stairway Chairlifts. REMOVE THE FOLLOWING LANGUAGE: for Vertical and Inclined Wheelchair Lifts and Stairway Lifts. Testing under sections 10.3.2 and 10.3.3 shall comply with § 405.8 (relating to periodic test results). (6) Electric wiring and apparatus shall comply with the ''ICC Electrical Code.'' (7) ASME A17.8-2016" REMOVE THE FOLLOWING LANGUAGE: for ADD THE FOLLOWING LANGUAGE: Standard for Wind Turbine Tower Elevators. | See Document E_6_NEII_PA-Comments_Elevator_Code NEII Comment: The major change is the adoption of A17.3 (2016), which governs the safety standards of existing elevators. The requirements included in this code represent the most critical upgrades for existing elevators in order to achieve the highest level of safety for elevator workers and the riding public. We have also included some editorial changes e.g. requirements are not sections per code. |  | No additional action on this line item. Public - concern was taking out section 5.3 for private elevators. We we need permits to approve private elavators? What code will we be applying. BOIS will provide some suggestions on regs according to Jennifer previously. 5.3 ???
Dylan Isenberg NEII | 2019-10-17 | § 405.2. Standards. | NEII SUGGESTS MODIFICATIONS TO THE FOLLOWING LANGUAGE AS FOLLOWS: (b) The following sections of [‘‘ASME A17.1-2000’’ with ‘‘A17.1b-2002’’ addenda] “ASME A17.1-2016” are not adopted as the Uniform Construction Code: (1) Section 5.3 (Private residence elevators). (2) Section 5.4 (Private residence inclined elevators). (3) Section 5.8 (REMOVE THE FOLLOWING LANGAUGE: Shipboard ADD THE FOLLOWING LANGUAGE: Marine elevators). (4) Section 5.9 (Mine elevators). (5) Section 7.7 (Automatic transfer devices). (6) Section 7.8 (Power dumbwaiter with automatic transfer devices). (7) Section 7.9 (Electric material lifts with automatic transfer devices). (8) Section 7.10 (Hydraulic material lifts with automatic transfer devices). (9) Section 7.11 (Material lifts with obscured transfer devices).] In the next section, replace the word Section with the word Requirement #10 - #25 (10)Section 8.6.7.3 (Private residence elevator). ([11] 10) Section 8.6.7.4 (Private residence inclined elevators). ([12] 11) Section 8.6.7.8 (Shipboard elevators). ([13] 12) Section 8.6.7.9 (Mine elevators). ([14] 13) Section [8.6.9.2] 8.6.10.2 (Material lifts and dumbwaiters with automatic transfer devices).] ([15] 14) Section 8.7.5.3 (Private residence elevators). ([16] 15) Section 8.7.5.4 (Private residence inclined elevators). ([17] 16) Section 8.7.5.8 (Shipboard elevators). ([18] 17) Section 8.7.5.9 (Mine elevators). ([19] 18) Section 8.7.7.3 (Material lifts and dumbwaiters with automatic transfer devices). ([20] 19) Section 8.10.5.2 (Private residence elevators and lifts). ([21] 20) Section 8.10.5.5 (Material lifts and dumbwaiters with automatic transfer devices). ([22] 21) Section 8.10.5.8 (Shipboard elevators). (22) 8.10.5.16 Mine Elevators. (23) Section 8.11.5.2 (Private residence elevators and lifts). (24) Section 8.11.5.5 (Material lifts and dumbwaiters with automatic transfer devices). (25) Section 8.11.5.8 (Shipboard elevators). | See Document E_6_NEII_PA-Comments_Elevator_Code NEII Comment: The major change is the adoption of A17.3 (2016), which governs the safety standards of existing elevators. The requirements included in this code represent the most critical upgrades for existing elevators in order to achieve the highest level of safety for elevator workers and the riding public. We have also included some editorial changes e.g. requirements are not sections per code. |  | Same as above
Dylan Isenberg NEII | 2019-10-17 | § 405.4. Approved designs, equipment and devices. | A platform, car, cabin or chair safety device may be installed after it receives a Department-issued certificate of acceptance. An applicant for a certificate of acceptance shall meet the following requirements: (1) The manufacturer, designer or engineer of the platform, car, cabin or chair safety device shall submit the design to the Department REMOVE THE FOLLOWING LANGUAGE: The Department will observe the operation and testing of the device for compliance with the Uniform Construction Code before [use of] the device is placed into service in this Commonwealth. ADD THE FOLLOWING LANGUAGE: A letter, certificate or listing by a national recognized third-party testing laboratory (NRTL) such as CSA, ETL Intertek, Liftinstituut or UL stating the safety device is designed and tested to meet or exceed all applicable requirements of the Uniform Construction Code. This must include the trade name or model number of the device and indicate the appropriate standard. A listing is valid only for the tested components. The Department will issue a REMOVE THE FOLLOWING LANGUAGE: certificate ADD THE FOLLOWING LANGUAGE: letter of REMOVE THE FOLLOWING LANGUAGE: acceptance ADD THE FOLLOWING LANGUAGE: approval REMOVE THE FOLLOWING LANGUAGE: after it observes successful testing ADD THE FOLLOWING LANGUAGE: to permit instalation of the device. | NEII Comment: The product acceptance process in the Commonwealth is the most burdensome in the entire country for both the Department and manufacturers. In order to streamline the process, the language above allows the Department to review certification letters from national third-party laboratories instead of traveling to a manufacturer’s facility out of state to witness a device before it can be installed in the Commonwealth. | Scope issue - no discussion needed .
Dylan Isenberg NEII | 2019-10-17 | 405.5 | The Department will conduct an acceptance inspection to confirm compliance with the Uniform Construction Code before a new elevator or lifting device or an elevator or lifting device under repair, ADD THE FOLLOWING LANGUAGE: or alteration , REMOVE THE FOLLOWING LANGUAGE: or modification is put into service. | See Document E_6_NEII_PA-Comments_Elevator_Code NEII Comment: There is no definition of “modification” in either ASME A17.1 or the UCC. | Scope issue - no discussion needed.
Dylan Isenberg NEII | 2019-10-17 | § 405.8. Periodic testing. | NEII COMMENT: NEII supports the proposed intervals for periodic testing outlined under 405.8 as they are in alignment with what is recommended by ASME A17.1/CSA B44 (“A17.1/B44”). However, the A17.1/B44 does not require weight tests every five years. Alternative testing is allowed by A17.1/B44 and there is no justification for restricting it arbitrarily. In fact, alternate testing eliminates the need for elevator mechanics to physically transport thousands of pounds of test weights in and out of buildings. Alternate testing is based on physics and has the potential to reduce strains and sprains, which are among the most common injuries for elevator workers. | See Document E_6_NEII_PA-Comments_Elevator_Code | Dealt with previously
Dave Perri | 11/8/2019 (Email) | City certified elevator inspectors. | Hi Basil: Hope all is well. Betsy will be at the hearing in Harrisburg on Tuesday. We have heard that some special interests desire the City of Philadelphia to license workers who repair, install, test and service elevators. We have no interest in doing that which would confuse and complicate authority for elevator safety. So that our testimony does not step on other’s toes or cause conflict can you let us know whether local licensing will be discussed? Thank you sir, DP | see Document Dave_Perri_Inspectors1182019
Norman Martin | 11/12/19 Public Comments and Submitted Written Comments | Process Comment | Adopt the latest edition of the ASME A17.1 Safety Code for Elevators and Escalators commonly referred to as the A17 without deviation... I want to reiterate the importance of adopting the most recent edition of the A17 model elevator code in order to improve safety and to cut regulatory yellow tape. There is no reason for Pennsylvania to continue lagging behind the rest of the country with one of the most outdated codes. | See Norman Martin written comments in public testimony for additional information
August Whymeyer | 11/12/19 Public Comments and Submitted Written Comments | Process Comment | ASME and other standard-developing bodies only establish recommendations in the form of standards. ASME does not enforce requirements. ASME does not claim or establish acceptance of the practice of applying requirements. They only become enforceable after a jurisdiction adopts a given code, and furthermore, only after a diligent and objective review of any given standard to ensure safety to their communities can be supported through its final revision in the jurisdiction. | See August Whymeyer written comments in public testimony for additional information
August Whymeyer | 11/12/19 Public Comments and Submitted Written Comments | Definitions | Definitions in the standards are generic at times and may not represent what needs to be achieved in the jurisdiction. For this reason, it is recommended that the definition of elevator personnel be revised to encompass not only the criteria in ASME A17.1 but also the working language to establish the proper training and qualified persons are performing work on complex electromechanical machinery our families, friends, and fellow passengers ride and use daily. We are not a licensed state, and therefore all the more reason to ensure trained, qualified personnel are established through our codes, once adopted. The definition should read as follows: persons who have been trained in the construction, maintenance, repair, inspection, and testing of equipment and are enrolled in or have completed a certified apprenticeship program approved by the Commonwealth of Pennsylvania. Personnel who have been established as levator personnel prior to the effective date of this statute, as defined by being awarded completion of a nationally-recognized elevator education program approved by the Commonwealth of Pennsylvania, and have at least five years unsupervised experience working in the elevator industry shall be considered elevator personnel.
August Whymeyer | 11/12/19 Public Comments and Submitted Written Comments | ASME A17.1-2016/CSA B44-16, any requirement such as 2.26.7 and 2.27.3.1.6 | In the 2016 edition of ASME A17.1, a change was published that no longer bypasses an in­car stop switch or an emergency stop switch when the elevator is recalling on Firefighters' Emergency Operation, Phase I. This is flawed due to several factors, the first being, despite it being a requirement that an in-car stop switch is restricted to only be in the possession of elevator personnel, elevator companies and other entities habitually provide these restricted keys to persons who should not have them. Furthermore, regarding emergency stop switch freight elevators, having operators who understand the restrictions on freight elevators are not consistent and the code requirements are not detailed enough to ensure a knowledgeable person would be in control of a freight elevator with an emergency stop switch when Firefighters' Emergency Operation Phase I is actuated. This would result in untrained persons stopping an elevator that an engineering control is operating to move the elevator to a safer location. The best scenario for any elevator recalling on FEO Phase I is to complete that operation. In addition, this ASME code change was not subject to code coordination wherein the timing of a shunt trip device, when installed in accordance with a recommendation by NFPA, is in effect. Please note that code coordination simply is not practiced despite claims that it is. Please take exception to this change in ASME A17.1-2016/CSA B44-16, any requirement such as 2.26.7 and 2.27.3.1.6 that in part no longer defeat the in-car stop switch and the emergency stop switch; they should remain defeated in that scenario. | NEII COMMENTS: In-car stop switches are required to be a Group 1 key so that they are only available to elevator personnel who are trained properly. They were removed from the A17.1 code many years ago for passenger security and safety. Emergency stop switches are allowed only in freight elevators with a trained operator. Elevator personnel and trained operators are able to evaluate the situation based on their training and should retain access to the stop switch during Phase I to allow them to control the movement of the car and prevent it from moving toward a hazard.
August Whymeyer | 11/12/19 Public Comments and Submitted Written Comments | Process | Please assemble your safety board or an ad hoc board to recognize, communicate, and ultimately adopt codes and standards only after a comprehensive review of the language, which in this case represents approximately 1,600 changes from that which is being enforced at this time.
August Whymeyer | 11/12/19 Public Comments and Submitted Written Comments | Not stated | Alternative Testing: Test it all the way. And it's been a test that's been in for hundreds of years and it still works. Look at alternative testing; B737s had alternative testing done to them and look at where we're at. Keep testing them the way they are. It's a proven fact that it works. | Reference Question and Answer from Public Testimony page 25, not in written testimony
Sam Clark | 11/5/2019 (Email) | Not provided | Fire Service Phase I & II controls a. Need for a universal fire service control key (for firefighters) b. Need to ensure these controls are actually being tested and are operational when inspections are performed 2. Car-Door Restrictors a. Briefing on what we have found in the field/need for them to be operational and not made to be inoperable b. Review of fatal incidents if needed or desired (direction from you preferred, one would be Penn State University incident in 2003) 3. Power Control Locations with regard to M.R.L.'s a. Problems encountered in the field b. Need for Fire Service to know location and have key access, prior to the incident I would desire to speak to the need for education of the Fire Service personnel across the Commonwealth. Having taught the specialty topic of elevator rescue for greater than 20 years, I am well tuned in to the needs and deficits of the emergency services with regard to elevator incidents. These are the three I had planned to speak on, and of course anything else I am requested to. Any input from you prior to the meeting is appreciated and welcomed. I have cc'd my supervisor Tom Cook, Administrator of the PA State Fire Academy, as well as PA State Fire Commissioner Bruce Trego. Thank you all for you support of efforts to improve PA. Samuel W. Clark - Fire Instructor, PSFA Assistant Fire Chief, Fort Indiantown Gap Fire & Emergency Services 717-598-5014 | See Sam1152019 See individual comments listed below
Samuel Clark | 11/12/19 Public Comments and Submitted Written Comments | Not stated | My recommendation to the PA Elevator Safety Board is to provide support in the form of endorsement and encouragement in the form of communications to the PA State Fire Academy that would foster basic educational programs for the emergency services personnel with regard to elevator emergencies, such curriculum to include elevator use during fire alarms and fires, and also occupant removals from stalled cars. Some of this may be done online, but to be sure, hands-on limited training is required to ensure competency. The demand for training is high for this type of topic. The instructor base is very small, very narrow. The Fire Academy has a program for many years established called Academy on the Road where a select group of PEMA, part-time Commonwealth employees, deliver on-the-road training. My basic thoughts are that the Fire Academy should provide a basic course one time every few years in ll 67 counties in Pennsylvania. This would foster a cultural change in the fire service approach to elevator use at not only fire events but at stalled cars. | See Samuel Clark written comments in Public Testimony for more details NEII COMMENTS: Location of the main line disconnect in addition to disconnecting of battery lower devices within A17.1 references NFPA-70(NEC), which is covered in very explicit detail within article 620.51. A17.1 inquiry 16-3025 in fact addresses the additional contact requirement to detect the removal of power to prohibit movement on battery power. MRLs are required to provide information for the location of the disconnects as per the National Electric Code. Manufactures and provide this information on their power data layout drawings. Also, note that local fire departments have information regarding the location of these disconnects and associated safety equipment by standard operating procedures
Samuel Clark | 11/12/19 Public Comments and Submitted Written Comments | Not stated | The topic is power shut-off locations for the newer MRL type elevators, the machine room-less. It seems there's no identified required location for the main drive power shut-off switch.It is paramount for safety reasons that main drive power be shut off, and the only acceptable location is the designed power control point for the elevator machine, the drive system, not an upstream breaker or a switch. The control point was found in the machine room typically, whether it was a hydraulic drive or whether it was a cabled-traction electric machine. When it comes to MRLs, we have no idea where this power control point may be. It appears, but I am uncertain, that the code does not require a standard location for power control points for the new MRL elevators. The fire departments need to know the location of the power control point for MRLs. They also need access to locked areas to control the power before beginning non-destructive techniques that are described in ASME A17.4. Wherever MRLs are installed, the location of the design power control point for the drive machine be communicated to the fire department, along with identification of any required keys to access this power control point. | See Samuel Clark written comments in Public Testimony for more details
Samuel Clark | 11/12/19 Public Comments and Submitted Written Comments | Not stated | Car door restrictors, as I understand it, have been required on new installs or significant upgrades in Pennsylvania since we adopted by reference the current version of ASME A17. I feel that enforcement of the code is paramount for life safety of occupants. Inspections should require that car door restrictors work. I think it's a sound reason why they're installed. | See Samuel Clark written comments in Public Testimony for more details
Samuel Clark | 11/12/19 Public Comments and Submitted Written Comments | Not stated | Fire Service Phase I and Phase II controls.With regard to that, there's two points about those controls. Number one, one of the largest single challenges to the fire service is that there's no standard key for these controls. I am aware that the proposed version of the code will in fact specify the FEO-Kl as a universal key. This is a good move, in my opinion, in the right direction, but it will not affect prior installs as grandfathering undoubtedly will be in place. hile as a fire chief I would love to see a retroactive requirement to change to this universal key, I do have an appreciation for costs associated with changing prior installs. So my comment to the Board is I do not recommend that prior installs be required to change to the universal key, don't feel that it was being considered, but I don't recommend that. What I ask is that you consider strict compliance with that universal key going forward in an effort to minimize the burden of how many keys we have to catalog. | See Samuel Clark written comments in Public Testimony for more details, See also questions from the public testimony on page 49 of the 11.12.19 Public testimony transcript where he said he would support this from a purely safety standpoint. Also reference Sam Clark's follow up email, where he does support this for prior installs in addition to new installs. Quote: Just a note to say thank you for having at the meeting. I think it was productive. I will say that two board members spoke to me after the meeting was over and asked if I would favor making a phase in period for all existing sites to convert to using the FEO-K1 fire service key that will be required if new code is adopted. I would favor that, I honestly did not think the Board would entertain that. I may put something in writing to distribute to the Board for their consideration. Again, thank you both. See Sam2_11142019
Samuel Clark | 11/12/19 Public Comments and Submitted Written Comments | Not stated | Phase I and Phase II Testing during inspections. I would encourage L&I to ensure that testing of Fire Service Phase I and Phase II is strictly enforced. | See Samuel Clark written comments in Public Testimony for more details
Michael Walsh | 11/12/19 Public Comments and Submitted Written Comments | Section 2.7.6.3.2 (e) | I would like to comment on the following two areas within this section of the requirement, 2.7.6.3.2(e), and 2.7.6.3.2(f). As stated above, 2.7.6.3.2(e) states: labeled/marked "AGP" in accordance with the requirements of CSA B44.l and ASME Al7.5 (see 2.26.4.2). The above refers over to the requirements of 2.26.4.2, which are as follows: Electrical equipment shall be listed/certified and labeled/marked. CSA B44.l/ASME Al7.5 defines the scope and applicable requirements for this listing/certification. Note: Enclosures for motor controllers installed outside the specified spaces listed in 2.7.6.3.2 will require the additional marking "AGP" (Accessible to the General Public) to indicate that the equipment enclosure is suitable for this application. My concerns with this requirement as written are the following, and I could be wrong on this; I haven't been able to find it. The State of Pennsylvania, under the UCC Construction Standards Utilized for the state, does not appear to have adopted ASME A17.5. So there's a conflict here with the code. I would recommend adopting A17.5 within the UCC Standards to promote coordination of this code as written. There are many instances within this adoption that need consideration with regard to the coordination of other codes. ASME Al?.1-2016 and previous versions do not define AGP, or Accessible to the General Public, within Section 1.3 of the definitions. Without truly defining AGP and what it means, it is left open for individual interpretation. AGP, Accessible to the General Public, needs to be clearly defined before adopting this section of the code. Defining it is essential for the safety of the general public. | Reference Michael Walsh written comments in Public Testimony
Michael Walsh | 11/12/19 Public Comments and Submitted Written Comments | Section 2.7.6.3.2 (f) | Provided with a sign in conformance with the requirements of ANSI Z535.2 or Canadian Standard CSA Z321, that shall be prominently posted on the inside, on the inside, of the motor controller cabinet door indicating in letters not less than 25 millimeters high, oor to be closed and locked when elevator personnel are not present at this controller." This sign should be prominently posted on the outside or on both sides of the controller door for all to see. This ensures that both the general public and elevator personnel are aware the door should be closed and locked at all times when elevator personnel are not at the controller. This will alert the general public of an unsafe condition if they observe the door open and unlocked. The concern here is for the public safety. The public, along with elevator personnel, need to know that the controller door should be closed and locked when elevator personnel are not present. Putting this sign nside serves no purpose as a warning. When the general public comes upon the controller with a partially closed door, not locked, how are they to know the door should be closed and locked? If the general public opens the unlocked door, it now becomes an unsafe and potentially fatal condition. Another matter is that each manufacturer has their own controller and door. Certain manufacturers have non-hinged doors on their controller. When elevator personnel remove the door, they cannot see the warning on the inside of the door because it's opposing them. Other manufacturers have controllers within the door buck itself. They have keyed access and are hinged, but again, the general public would not be able to see the warning until opening a potentially unlocked door, putting themselves into an unsafe condition. | Reference Michael Walsh written comments in Public Testimony
Michael Walsh | 11/12/19 Public Comments and Submitted Written Comments | Section 2.12.7 - 2.12.7.2.l(c) | Section 2.12.7.2 addresses the location and design of the switches. It states: hoistway access switches shall conform to 2.12.7.2.1 through 2.12.7.2.5. 2.12.7.2.1. The switch shall be installed a minimum of 1,200 millimeters, or 48 inches, and a maximum of 1,825 millimeters, or 72 inches, above the floor measured to the centerline of the switch, adjacent to or part of the hoistway entrance at the landing with which it is identified, and in one of the following locations: (a) on the wall outside of the hoistway within 300 millimeters, or 12 inches, of the entrance frame; (b) on the hoistway entrance frame or jamb; and (c) on the sight guard. My recommendation is to exclude 2.12.7.2.l(c) from this adoption, on mounting it on the sight guard. The sight guard is attached to the landing door. These sight guards, along with doors, are under constant contact with the riding public. The sight guard is one of the most weakest parts of the moving door. Installing the access switch to the sight guard presents numerous areas of safety concerns. Most sight guards are affixed to the landing door utilizing self-tapping screws. Over time, from being hit, he sight guard tends to bend and/or loosen. Sight guards alone have caused many an elevator to be damaged as a result of the sight guard falling off. Introducing the access switch to an already known hazard just increases the potential for injury. Hoistway access switches have been part of the code for many years. Installing them in the door buck or adjacent to the door has been an effective installation method for many years. Introducing an electrical switch to a moving door creates a potential hazard of the cord being damaged or caught by the moving elevator or door and torn off. This is an active circuit that, if exposed, creates an electrocution hazard if the riding public were to come in contact with the live wiring. This switch mounted on the sight guard also presents the possibility for nuisance shutdowns and ground faults if the writing were to become exposed. For the elevator personnel operating the hoistway access switch mounted on the sight guard, there is the risk of being struck by the moving elevator while operating the key switch. From the location of the sight guard to the moving elevator is approximately two inches. The average width of the human hand is three inches. Mine's a little bit bigger. When you turn the elevator key in either direction, you are constantly at risk from the moving elevator. Introducing keys along with others on a key ring and the risk of getting the keys or ring caught on components attached to the moving car are greatly increased. | Reference Michael Walsh written comments in Public Testimony
Michael Walsh | 11/12/19 Public Comments and Submitted Written Comments | 2.12.7.2.2 | While considering removing 2.12.7.2.l(c) from adoption, please also remove 2.12.7.2.2 as well, as it only pertains to mounting the access switch on the sight guard. The code reads: where the switch is located on the sight guard, the sight guard shall accommodate and support the load of the switch and its wiring. So if we remove the first, the second should come out as well. | Reference Michael Walsh written comments in Public Testimony
Michael Walsh | 11/12/2019 Question and Answer with Board | None Stated | Chairman Weiant - What is your standard interpretation of AGP; have you seen any different interpretation of that in the past; and do you think we need a definition, a standardized definition of AGP? Mr. Walsh - I really do, and that's what I said there. I did research, Google, Alexa, and you cannot find a true definition for accessible to the general public. The closest I came to was readily accessible to the general public, which refers to communications, has nothing to do with elevators. Its important to define it because right here in this room, are we all the general public? I would say yes, but when it comes to this building, the people that work in this building, are they the general public? It's left to interpretation, and anything that you leave to interpretation, it's the guy standing there at that moment that makes the decision is it or is it not accessible to the general public, and once he makes that determination, or she, it creates a situation where all responsibility at that point falls on their shoulders, and that's not a good place to be. | In response to question by Chairman Weiant, additional discussion found on pages 64-68 of the public testimony transcript from 11.12.19
Kevin McGettigan | 11/12/19 Public Testimony | Process | I'm here to speak on the code that you're here to review and promulgate. One size does not fit all. We heard NEII get up here and testify as to how safe this code s and the process under which it goes forth. I'm here to tell you that that might have been the way code used to operate. Code now operates under convenience. Unfortunately, that's true, and if this body, if this Board accepts code as written, without at least trying to promulgate what you need to do as far as additions, deletions, or modification of that code, it would be reckless. One size does not fit all. You are not the same here as you are in California, as you are in Kansas, as you are in Massachusetts. | Note: No written testimony received, see public testimony transcript from 11.12.19 as reference
Kevin McGettigan | 11/12/19 Public Testimony | A17.7 | In adopting the code, there's a provision in there that automatically auto adopts A17.7. Now, A17.7, for those of you that don't know, is a performance-based code, it's not a prescriptive code, and the manufacturers have argued that we need some sort of code to try to invent these ew products and be able to bring these products to bear on the market. Well, the issue that I have with that is that it completely takes you out of the decision-making process. While different states have adopted A17.7 in some form, a lot of states have either removed it or limited its capacity to be an inforrna tional code only. If A17.7 is the code of choice for a manufacturer, then let them come here and present A17.7 to this body and you can give them a variance. Whether that's a blanket variance or not, that's up to this body.
Kevin McGettigan | 11/12/19 Public Testimony | Not stated | The way that we test elevators today saves lives. If we move to alternative testing, it's not going to be safe for the Commonwealth. | Additional details in the public testimony transcript from 11.12.19 pages 71-72
Kevin McGettigan | 11/12/19 Public Testimony | Not stated | I have also heard some fire service testimony on fire service keys. I come from a state that has one key. That one key is in every single fire truck. I've heard some testimony on not making this retroactive for fire service because of cost. also heard some fire service testimony on fire service keys. I come from a state that has one key. That one key is in every single fire truck. I've heard some testimony on not making this retroactive for fire service life, its worth the cost | Additional details in the public testimony transcript from 11.12.19 pages 71-72
Kevin McGettigan | 11/12/19 Public Testimony | Not stated | I also come from a state that, prior to an elevator being turned over, they are required, the company is required to bring fire services to that job and operate fire service for them on that particular elevator. I hope you consider that, because I believe it to be a life-saving measure | Additional details in the public testimony transcript from 11.12.19 pages 71-72
Kevin McGettigan | 11/12/19 Public Testimony | Not stated | I also heard the statement that was given about harmonization with other building codes. I'm not quite sure of the authority that Pennsylvania has here, but the building department in most states have the ultimate word, and when you conflict with their codes, they don't care. As much as you want to try to come into harmonization with them, there is no harmonization with some of these other building codes, they are the authority at that point, and we go back and forth from one inspector to another, one saying "take this out" and the other one saying "put this in," so it is something that we're going to have to look at. | Additional details in the public testimony transcript from 11.12.19 pages 71-72
Kevin McGettigan | 11/12/19 Public Testimony | 3.4.1 | Lastly, I want to get into 3.4.1. The Board had made a decision on this, and this is bottom car clearance. Some of the things that I'm about to day might give some people a red ass, I really don't care, I think they need to be said. I think that what the Board heard for testimony from a Thyssen representative concerning 3.4.1 was either (a) not truthful, or (b) the person is inept that was giving the testimony. This Board made a decision based on estimonies, and we were given three minutes to reply. I would ask this Board that you seek out and you identify 3.4.1 and you clarify it to the best of this Board's ability to make sure that these elevator constructors, when this car is on a fully rested compressed buffer, have a minimum of 24 inches, and if they want less than that 24 inches, they need to seek a relevant relief from this Board. .4.1, for the Board members that recall, is a 24-inch minimum clearance. 3.4.1.2 is the exceptions to which that clearance can be reduced. Thyssen Elevator, in 2014, made a revision to code trying to reduce that 24 inches and trying to make that a reduced amount or an exception within code. They failed. In 2014, and on 01/20/2015, it went out for letter ballot. The industry as a whole, as you heard in earlier testimony, takes these into consideration and there has to be consensus. On 04/07/2015, it went back out for letter ballot. The industry took that consideration; it failed. on 9/24/2016, the proposal was tabled until a task group was considered. That task group moved on to 2017, in which the actual proposal was modified, and once again, it failed. Now, the reason I bring this up is under 3.4.1.2, they tried to add letter (d) hydraulic machine ounted on the pit floor. This is what they wanted to be able to make sure that there was under a 24 inch clearance on. Their rationale --and I apologize that I can't share any of the information with you in paper form, but make no mistake about it, as the authority having jurisdiction, if you write a letter to ASME requiring this information in order for you to make a determination on code that you're promulgating, they will supply it. The rationale that was given when this whole thing went down was clarifying clearances and marking requirements when a hydraulic machine is mounted in the pit. Now, while this body has given approval for hydraulic machines to be mounted in the pit --and I don't take exception to that; you do that for numerous reasons, whether it's cost, safety, or anything else. Like I said, I sat on a board for nine years and I understand what you're up against. I do want you to know, though, based on the information that was given to you, and based on that information you had to make a decision, the information you received was erroneous. | Additional details in the public testimony transcript from 11.12.19 pages 71-72
Jack Koch | 11/12/19 Public Comments and Submitted Written Comments | A17.1-2016, 2.7.5.4 | Please delete language in A17.1-2016, 2.7.5.4, which allows working platforms in the path of a car or counterweight and any related language allowing any nstallation to have equipment or structure that would service and test an elevator while putting affected persons in harm's way. | Reference Jack Koch written comments in Public Testimony NEII COMMENTS: Working platforms are used to provide safe and convenient access to components in the hoistway that require inspection, maintenance, repair and replacement. The ASME code requires retractable stops and electrical protective devices (EPDs) and other explicit protections. EDPs are accepted as protection from car movement for other code requirements. Moreover, the working platform electrical protective device is assigned the highest safety level in the code – a SIL rating of 4 based on an IEC risk assessment process.
Jack Koch | 11/12/19 Public Comments and Submitted Written Comments | ASME A17.1-2016, Section 5.10 | any elevator being granted a Certificate of Operation in compliance with ASME A17.1-2016, Section 5.10, Elevators Used for Construction, or what is generally referred to across the United States as a temporary permit. We utilize this routinely in the State of Pennsylvania on construction, demolition, and modernization job sites. Compliance with ASME A17.l-2016 is important, and I would like to clarify these elevators and the site conditions are not conducive to safe public use. Their use is restricted to construction or demolition to provide transportation for construction personnel, tools, and materials only. Until full compliance with ASME A17.1, part 2 or 3, is achieved, they are not accessible to the general public. These elevators in this configuration should only be permitted to operate by having an attendant who meets the definition of elevator personnel, as modified by Mr. Whymeyer's testimony. Elevator manufacturing, buildings owners, and persons invested in the safe care of both equipment and persons using it have expressed the need to ensure these are restricted to code allowances and that an attendant be qualified to ensure the safe loading, use, and unloading of this conveyance type. | See additional detaisl in Jack Koch written comments in Public Testimony , Additionally, pages 82-90 contain question and answer related to this public testimony that should be reviewed by someone to determine if they relate to a new concept or the original written suggestion
Scott Hultstrom | 11/12/19 Public Comments and Submitted Written Comments | A17.1-2016 in Section 1.3. | I recommend that you revise the definition of sound engineering as follows. Sound engineering process the use of engineering or technical methods founded and employed based on safe engineering to recognize needs, hazards, and evaluate a device or system, its components, materials, as well as its application by taking into account relevant factors that may influence its potential hazards, hierarchy of hazard control, efficacy, and operation. This practice also involves the use of applicable standards, specifications, codes, regulatory and industry guidelines, providing the criteria as well as safe engineering and design methods, installation and maintenance practices. The rationale for this recommendation is to ensure a safety code provides consistency in its language, indicating understanding, recognition, acceptance, and utilization of safety codes and standards such as OSHA's Recommended Practices for Safety and Health Programs, to which the State of Pennsylvania's employers are bound. | Reference Scott Hultstrom written comments in Public Testimony NEII COMMENT: NEII strongly recommends that Pennsylvania retains the definition in ASME A17.1/CSA B44 (‘A17.1”) for consistency with the national standards. OSHA’s Recommended Practices for Safety and Health Programs is not a safety code or standard as indicated in the rationale above and does not contain any design requirements.
Scott Hultstrom | 11/12/19 Public Comments and Submitted Written Comments | A17.3-2015 | Please ensure to retain ASME's A17.3-2017, which is the latest edition that aligns with ASME A17.1-2016. When this is done, it must be done in accordance with what is recommended and follow a process that brings its enforcement to bear on the jurisdiction but mitigates impact. Any argument to not accept this is derived from an individual who is not trained in safety processes. The jurisdiction should assemble its AHJ, based on what I see here, specifically its Elevator Safety Board, who would act in accordance with Pennsylvania's Act 68 2018, Section 2214, to start the process, including determining the date existing installations must conform to the requirements. It is recommended that a local committee, consisting of representatives of groups directly interested, augment the Elevator Safety Board as needed in an ad hoc status to study the existing local conditions and to determine the length of time existing installations should be given between adoption of this code and compliance with each provision. Representatives of the following groups should be considered for serving on such a committee: building owners; real estate management companies; architects and consulting engineers; manufacturers of the equipment; maintenance companies; insurance companies; city and state enforcement officials; elevator labor unions, etc. Populate additional persons as needed. Plan it, implement it in pieces, do not negate it to save money. Money won't be saved, only safety will be negated. The rationale for this is the hazards that exist on existing equipment are numerous enough to warrant utilizing a retroactive approach. Despite legacy equipment faring better than newer equipment for reliability, there is value in adopting through a process and ultimately enforcing ASME's A17.3-2015. This increases safety to a community while lowering costs to a building owner. | Reference Scott Hultstrom written comments in Public Testimony
Scott Hultstrom | 11/12/19 Public Comments and Submitted Written Comments | A17.7 ASME A17.7-2007/CSA B44.7-07 | Please take exception to adopting A17.7 ASME A17.7-2007/CSA B44.7-07 Performance­based Safety Code for Elevators and Escalators. This standard preexisted in revisions and adoptions in many jurisdictions thus far but without clear understanding. The position of negating its inclusion moving forward, as with any change in a status quo, should be guided with objective observation, measurement, assessment, planning, and ultimately safety provisions to multiple sets of affected personnel. Observations of A17.7 show historically it being sold as an innovation to provide safety while keeping pace with technology. What has precipitated is the utilization of this standard to rubber stamp new technology, with no practical application of safety to affected persons being considered, developed and enforced. This standard provides an incomplete listing of hazards/risks and no further guidance beyond that to practically apply safety measures, and therefore it is not equivalent to a prescriptive standard such as A17.1. Plans moving forward is to advocate for safety, as we always have done. When A17.7 is brought to bear on any scenario, we will vet it against fundamental safety processes we have come to utilize to filter hazardous variables from our culture. As in the past, it is expected that A17.7, although somewhat sound in principle, will be shown to provide only monetary gains to employers at the expense of the safety of their employees and those who would ride our work. In one case history, A17.7, Performance-based Safety Code for Elevators and Escalators, was used to bring conveyances on a large-scale job site into the community. Forty-five unmitigated, uneliminated hazards were identified but never addressed, required Certificates of Conformance advertised as required publicly were spontaneously indicated to be invalid by the accredited elevator\escalator certifying organization -- also known as an AEECO and ultimately it was reported that the A17.7 claimed safe conveyances were turned over, allowing the public to use them somewhere between nine days and five weeks before being certified after the fact. The A17.7 safety standard does not establish equivalent safety requirements as compared to prescriptive standards. | Reference Scott Hultstrom written comments in Public Testimony
Scott Hultstrom | 11/12/19 Public Comments and Submitted Written Comments | Section 2.7 | With regard to Section 2.7, Machinery Spaces, Machine Rooms, Control Spaces, and Control Rooms, revise as follows: the requirements of 2.7.5.1 through 2.7.5.1.4 shall be complied with if the elevator driving-machine brake, emergency brake, elevator motion controller, or motor controller are located inside the hoistway. Further, I want to revise 2.7.5.1.1 to read: during maintenance, repairs, replacements, tests, or inspection of the elevator driving-machine brake, emergency brake, elevator motion controllers or motor controllers located inside the hoistway from inside the car or from the car top, a means to prevent unexpected vertical movement shall be provided. The rationale for this proposed revision is the hazard of unexpected movement of machinery in this scenario always exists for MRLs. Permissive and subjective language should be revised to mitigate/eliminate the potential for, but not limited to, OSHA Focus Four hazards of struck by, caught between, falls, and electrocution due to unexpected vertical movement. | Reference Scott Hultstrom written comments in Public Testimony NEII COMMENTS: The American Society of Mechanical Engineers (“ASME”) conducted a Hazard Assessment and vetted all code changes related to the additional equipment in the hoistway through a thorough consensus process. The code language was based on the results of the Hazard Assessment. This language was added to the code since the 2005 supplement version and is identical in the 2016 version. Contrary to the public comment, unintended movement does not always exist with MRLs. Further, protection from unintended car movement while working on the car top is no less important for a non-MRL elevator as it is for an MRL elevator. While working on the car top, the car top inspection operating device and the car top stop button control the machine brake and power to the motor for MRL and non-MRL elevators. Additional protection for an MRL against unexpected car movement is necessary only if maintenance of the machine and emergency brakes, and/or a motor controller located in the hoistway can cause unexpected car movement. Where these components require no maintenance other than replacement, typical field practice to restrain the car can be provided during the replacement action. Protection from unexpected vertical movement is important if it can occur, which is only if maintenance requires adjustment to the machine and emergency brakes, and/or motor controller from inside the hoistway. The A17.1 code addresses these conditions; therefore the current language should be maintained. ASME A17 Inquiry 06-26, below, further clarifies this requirement
Scott Hultstrom | 11/12/19 Public Comments and Submitted Written Comments | Section 1.3, Definitions | In Section 1.3, Definitions, add the following definition. Controller, AGP: A device or group of devices that serves to control, in a predetermined manner, the apparatus to which it is connected and wherein any portion of the AGP controller is accessible or exposed to the general public at any time. Rationale to define equipment that may present hazards to untrained personnel. Section 2.7, Machinery Spaces, Machine Rooms, Control Spaces, and Control Rooms. | Reference Scott Hulstrom public testimony from public testimony transcript dated 11.12.19 NEII COMMENTS: A definition is not needed because AGP is not a type of controller. AGP refers to a sign that means “Accessible to the General Public”. When a controller is located in an area that is accessible to the general public it has to meet additional requirements, including a sign which indicates that it meets those requirements. The term “Accessible to the General Public” is spelled out in the notes to Requirement 2.26.4.2. In addition, the controller door is required to be opened only with a Group 1 security key, meaning it can only be unlocked by elevator personnel who are trained. The Group 1 security is of a higher level of security than access via Group 2 security key to Machine Spaces/rooms and Control Spaces/rooms. Therefore, additional signage is unnecessary because elevator personnel should already be familiar with how to safely access control systems.
Scott Hultstrom | 11/12/19 Public Comments and Submitted Written Comments | Section 2.7 | Section 2. 7 Machinery Spaces, Machine Rooms, Control Spaces, and Control Rooms, revise 2.7.6.3.2(e) as follows: 2.7.6.3.2 The motor controller shall be located in a machinery space, machine room, control space, or control room. A motor controller shall be permitted to be located outside the specified spaces, provided it is enclosed in a locked cabinet. The locked cabinet shall be (e) labeled/marked "AGP" in accordance with the requirements of CSA B44.1/ASME A17.5 (see 2.26.4.2) and the requirements of this code. Rationale: To ensure a motor controller in or exposed to a public area at any time that may present hazards to trained and untrained personnel is properly marked. This revision reiriforces and is reiriforced by the proposed definition of AGP Controller. Access and worldng space has to be provided and maintained about all electrical equipment to permit ready and safe operation and maintenance of such equipment. Additionally affected persons in a public area have to be protected. | Reference Scott Hultstrom written comments in Public Testimony NEII COMMENTS: The additional wording is redundant and unnecessary because all equipment covered by this code has to meet the requirements of this code. If it is added here and not in every other section does that imply that the other sections do not need to comply? A17.1, combined with NFPA 70 (NEC) provides sufficient labeling.
Scott Hultstrom | 11/12/19 Public Comments and Submitted Written Comments | Section 2.7 | Definition of AGP, so we would be inclusive of adding the requirements in this code, which would include AGP. I will make a note that this requirement I want revised does reference A17.5. I was not aware that you did not adopt A17.5 in this jurisdiction and I don't need an answer, it's a question for you. The fundamental question you should ask yourselves is you are not certifying electrical equipment for elevators and escalators in accordance with CSA, or ASME A17.5 in this case. I don't know how you achieve certified equipment, and if you don't have certified equipment, that's a big problem. So I don't know what you're using as equivalent to A17.5, but that is deeply concerning me. Revise 2.7.6.3.2(f) as follows: 2.7.6.3.2 2.7.6.3.2 The motor controller shall be located in a machinery space, machine room, control space, or control room. A motor controller shall be permitted to be located outside the specified spaces, provided it is enclosed in a locked cabinet. The locked cabinet shall be (f) provided with a sign in conformance with the requirements of ANSI Z535.2 or CAN/CSAZ321, that shall be prominently posted: (1) on the inside of the motor controller cabinet door (2) indicating in letters not less than 25 mm (1 in.) high, (3) "DOOR TO BE CLOSED & LOCKED WHEN ELEVATOR PERSONNEL ARE NOT PRESENT AT THIS CONTROLLER." ( 4) Procedures for maintenance, repairs, replacements, and tests performed by elevator personnel shall be provided (See 8.6.1.4.1) Note: Equipment in an area accessible to the general public may present hazards addressed in additional codes and standards such as but not limited to the model building codes and OSHA regulations. Rationale: To ensure applicable procedures related to a motor controller in or exposed to a public area at any time that may present hazards to trained and untrained personnel are provided. Access and working space has to be provided and maintained about all electrical equipment to permit ready and safe operation and maintenance of such equipment. Additionally affected persons in a public area have to be protected. In this area several standards have been found to be in conflict that may result in a reduction to life, limb and the welfare of affected persons. Contact me if this is in need of further explanation as a physical meeting is warranted to adequately address the quantity and quality of this sensitive area. | Reference Scott Hultstrom written comments in Public Testimony NEII COMMENTS: This request is redundant. Procedures for maintenance, repair, replacements and tests are addressed in Part 8 of the code, including completion of work that may be exposed to a public area, and are applicable to all section of the code, not just Part 2. It is not necessary to include requirements here. All On-Site Documentation and Maintenance Control Programs should be located per the requirements in Part 8.The public comments fail to provide any examples of conflicting standards or detail on how the “life, limb, and the welfare of affected persons” have been reduced nor has anything on this subject been presented to the subcommittee for A17.1 standards. No additional wording changes are necessary as this is sufficiently addressed in ASME A17.1 code.
Scott Hultstrom | 11/12/19 Public Comments and Submitted Written Comments | 2.7.6.3.2(g) | Section 2. 7 Machinery Spaces, Machine Rooms, Control Spaces, and Control Rooms, add 2.7.6.3.2(g): 2. 7 .6.3 .2 The motor controller shall be located in a machinery space, machine room, control space, or control room. A motor controller shall be permitted to be located outside the specified spaces, provided it is enclosed in a locked cabinet. The locked cabinet shall be ADD THE FOLLOWING LANGUAGE: (g) Electrical clearance requirements shall comply with NFP A 70, NFP A 70E, 29 CFR 1926 or 29 CFR 1910, whichever is applicable (see Part 9). In the event two or more code requirement(s) conflict, the requirement(s) providing a higher degree of safety shall be used. Rationale: To ensure a working space in proximity to a motor controller in or exposed to a public area at any time that may present hazards to trained and untrained personnel is provided. Access and working space has to be provided and maintained about all electrical equipment to permit ready and safe operation and maintenance of such equipment. Additionally affected persons in a public area have to be protected. In this area several standards have been found to be in conflict that may result in a reduction to life, limb and the welfare of affected persons. Contact me if this needs further explanation as a physical meeting is warranted to adequately address the quantity and quality of this sensitive area. | Reference Scott Hultstrom written comments in Public Testimony NEII COMMENTS: Not necessary as 2.26.4.1 & 2.26.4.2 references NFPA 70 (NEC) and ASME A17.5 for appropriate electrical codes that capture appropriate requirements for worker safety as required by Fed OSHA references 29 CFR 1926 & 1910. Adding the OSHA references to part 9 of ASME A17.1 would create additional confusion as they are generic requirements rather than more specific performance requirements as listed in NFPA 70 (NEC) and ASME A17.5.
Scott Hultstrom | 11/12/19 Public Comments and Submitted Written Comments | Part 9 | I would urge you to consider Part 9, Reference Codes, Standards, and Specifications, ADD THE FOLLOWING LANGUAGE: (g) Electrical clearance requirements shall comply with NFP A 70, NFP A 70E, 29 CFR 1926 or 29 CFR 1910, whichever is applicable (see Part 9). In the event two or more code requirement(s) conflict, the requirement(s) providing a higher degree of safety shall be used. Rationale: The State of Pennsylvania, its jurisdictions and its contractors and separate jurisdictions operating within the state 's boundaries are warranted, to comply with not only established codes and standards but, based on various factors to comply with one or all of the proposed referenced standards. | Reference Scott Hultstrom written comments in Public Testimony NEII COMMENTS: These standards are not referenced by this code and therefore do not belong in the list of referenced standards. The standards listed in NFPA 70E and the other referenced sections are not equipment standards. Instead, they are standards related to how workers interface with the equipment. These standards are addressed in the Elevator Escalator Field Employee Safety Handbook that is referenced by ASMEA17.2 (Inspector Guide).”
Scott Hultstrom | 11/12/19 Public Comments and Submitted Written Comments | Section 2.12 | Section 2.12 under Hoistway Door Locking Devices, I'm not going to bore you with the details, somebody already made the comment. All I'm asking you is to strike the provision to allow a hoistway access switch on a sight guard. The ad lib is, for all intents and purposes, a hoistway door panel is an electrically-isolated thing because of elastomers, such as neoprene, on rollers, and Delrin and other insulators on gibs. That being said, if you put an electrical piece of equipment on a sight guard, it could result in chafing of the SO cord that goes to that device, it could result in the door panel becoming live. If that happens, somebody could actually come in contact with an energized source. REMOVE THE FOLLOWING LANGUAGE: (c) on the sight guard Rationale: As the distance between a human body and a hazard decreases the risk increases. This inverse relationship is a foundation of safety and is compounded by this requirement wherein the distance from a human body is to elevator equipment of substantive size and mass. There has been at least one accident in recent years resulting in an employee suffering a career ending injury related to this scenario created at least in part by engineering design. | Reference Scott Hultstrom written comments in Public Testimony NEII COMMENTS: In order to improve safety, changes were made to this requirement in the 2016 edition of A17.1 limiting where an access switch could be located. The sight guard is outside the line of movement of the elevator and therefore should not create any new hazards. A similar comment was received and taken into consideration during the ASME process. During access operation, the elevator speed and travel are limited. Also, the key switch can be operated only by trained elevator personnel (Group 1 key) who are cognizant of the elevator’s movements. These factors mitigate the potential hazard. Lastly, the description of the referenced accident in the public comment is too generalized to make even a threshold assessment as to whether it is at all relevant to this provision, let alone whether the location of the switch on the sight guard and/or any engineering design caused or contributed to the alleged injury. Also, such an accident was not presented during the subcommittee for A17.1 standard which is the appropriate forum to raise concerns.
Scott Hultstrom | 11/12/19 Public Comments and Submitted Written Comments | Section 2.12 | Section 2.12 Hoistway Door Locking Devices & Electric Contacts, & Hoistway Access Switches in requirement, delete requirement 2.12.7.2.1: REMOVE THE FOLLOWING LANGUAGE: 2.12.7.2.2 Where the switch is located on the sight guard, the sight guard shall accommodate & support the load of the switch & its wiring. Rationale: If the 2.12. 7.2. 1 (c) requirement is deleted then this has no further meaning. In addition to the previous comment's rationale concerns of engineering an electrical component onto a hoistway door assembly that is for the most part electrically isolated may result in the assembly becoming energized posing a hazard to the riding public. This engineering design is in conflict with the afore mentioned comment on sound engineering in that it may increase the frequency of a worker operating in a location conducive to an OSHA Focus Four Hazard. | Reference Scott Hultstrom written comments in Public Testimony NEII COMMENTS: This requirement should be retained along with 2.12.7.2.(c). Requirement 2.12.7.2.2 ensures the sight guard is designed to accommodate and support the switch and wiring. The concerns expressed regarding the electrical equipment are address by Requirement 2.12.7.2.1 which does not allow any single ground or short to render the interlock, gate switch, or combination lock to be ineffective where the hoistway access switch wiring moves due to door opening and closing. Any concerns raised by the Submitter related to the recent change should be raised within the ASME A17.1 Hoistway Committee.
Scott Hultstrom | 11/12/19 Public Comments and Submitted Written Comments | Section 8.7 | Section 8.7 Alterations delete the following: REMOVE THE FOLLOWING LANGUAGE: 8.7.2.14.5.2 Where conformance with 2.14 .1.7 is not possible due to existing overhead conditions, a stowable design, e.g., foldable or collapsible, shall be permitted provided that (a) when the railing is in the fully stowed position, the car shall be permitted to operate in any mode of operation except top of car inspection operation. (b) when the railing is in the fully extended position, the car shall be permitted to operate only in top of car inspection operation in accordance with 2.26.1.4.2. (c) when the railing is neither stowed nor in the fully extended position, the car shall not be permitted to operate. (d) switches used to monitor the stowed position shall have contacts that are positively opened mechanically when the railing is moved from its stowed position. (e) switches used to monitor the fully extended position shall have contacts that are positively opened mechanically when the railing is moved from its fully extended position. (I) the occurance of a single ground, or the failure of a contactor, a relay , or any single solid state device, or a failure of a software system in the circuits incorporating these switches shall not permit operation other than as specified in 8.7.2.14.5.2(a), (b), or (c). (g) means shall be provided to prevent upward movement of the car beyond the point required to maintain top of car clearances when the railing is not in the fully stowed position. Activation of the means shall not cause an average retardation exceeding 9.81 m/s2 (32.2 ft/s2). (h) vhen in the fully extended position, the railing shall meet the requirements of 2.10.2, and shall be designed to prevent accidental disengagement. (i) the force required to extend or retract the railing shall not exceed 220 N (50 lbf). Rationale: This requirement introduces a hazard by modifying an engineering control that may result in reduced vertical clearance that will result in an OSHA defined focus four fatality of struck by or caught between. Additionally it will result in an OSHA defined focus four fatality of a fall. An employer in The United States to include its territories would be legally in violation of imminent danger violations of 29 CFR 1910, Subpart D and I and 29 CFR 1926 Subpart M In essence a building owner would have purchased an elevator no one could safely and legally access the car top of | Reference Scott Hultstrom written comments in Public Testimony NEII COMMENTS: This requirement is in the Alteration section of the code and these railings are only allowed on existing equipment where full compliance with 2.14.1.7 is not possible. In some situations, the existing overhead may not allow for the installation of a fixed railing, so an alternative is provided to allow for a stowable design. A collapsible railing is preferred to no railing on some older equipment. The code requires the railing to be in place before elevator personnel can operate the equipment and ride the car top in inspection mode. Therefore, it provides equivalent safety to a fixed railing when it is deployed.
Scott Hultstrom | 11/12/19 Public Comments and Submitted Written Comments | 6.1.6.3 | 6.1.6.3 .6 Escalator Skirt Obstruction Device revise as follows: Means shall be provided to cause the electric power to be removed from the escalator driving-machine motor and brake if an object becomes caught between the step and the skirt as the step approaches the upper or lower combplate. The device shall be located at a point at which the step assumes a flat step position (see 6.1.3.6.5). The escalator shall stop before that object reaches the combplate with any load up to full brake rated load with escalator running [see 6.l.3.9.3(a)(2) and (b)(2)]. The device shall be of the manual reset type REMOVE THE FOLLOWING LANGUAGE: or it shall be permitted to automatically reset not more than one time within 24 hr of operation and thereafter require a manual reset before the next restart. Interruption of pm.ver during operation should not cause the device to lose the status of the timer nor the count of events. Rationale -Permitting an Escalator Skirt Obstruction Device to automatically reset one time within 24 hours of operation lowers the minimum safety standard. The ability for an electromechanical machine to effectively rule out a hazardous condition being present as opposed to elevator personnel ruling out the presence of a hazard has not been proven to ensure safety to the riding public. | Reference Scott Hultstrom written comments in Public Testimony NEII COMMENTS: Some protective devices previously required manual reset but can be visually examined externally and can be allowed to be self-resetting with occurrence restrictions. Contrary to the public comment, the automatic reset of the safety device can only take place if the obstruction has cleared the device (i.e., has been removed) and therefore the hazard is no longer present. It needs to also be highlighted that when the device is actuated (i.e., has been tripped), the equipment will stop and require an authorized person to restart the conveyance in accordance with normal starting procedures, which require them to confirm the conveyance is clear and there are no passengers on board. In other words, an authorized person with the appropriate experience must perform a visual inspection. It is known that if there is a failure of the safety function, repetitive shutdowns will occur in a short period of time. These shutdowns increase the possibility of falls when all riders must walk up and down an escalator. Therefore, the function was added to require a manual reset and, therefore, onsite intervention by elevator personnel in case there are two shutdowns within a 24-h time period of operation. The requirement of two shutdowns is based on experience and field trial. The function to require a manual reset in case there are two shutdowns within a 24-h time period of operation was also added to the self-resetting escalator skirt obstruction device (6.1.6.3.6) and the step upthrust device (6.1.6.3.9). This will provide additional safety to these devices as multiple shutdowns within a relatively short period of time will indicate a more serious issue with the equipment that will require onsite intervention by elevator personnel. ASME has determined the current code language offers enhanced safety when compared to the option of permitting the general public to use the non-operating escalator as a stairway until qualified personnel can arrive to reset the escalator.
Scott Hultstrom | 11/12/19 Public Comments and Submitted Written Comments | 6.1.6.3.9 | 6.1.6.3 .9 Step upthrust Device revise as follows: Means shall be provided in the passenger-carrying line of the track system to detect a step forced upward in the lower transition curve at or prior to the point of tangency of the horizontal and curved track. The means shall actuate when the riser end of the step is displaced upward more than 5 mm (0.20 in.) at the lower landing. Actuation of the means shall cause power to be removed from the driving-machine motor and brake. The escalator shall stop, before the detected step reaches the combplate with any load up to brake rated load with escalator running [see 6.l.3.9.3(a)(2) and (b )(2)]. The device shall be of the manual reset type REMOVE THE FOLLOWING LANGUAGE: or it shall be permitted to automatically reset not more than one time within 24 hr of operation and thereafter require a manual reset before the ne}(t restart. Interruption of power during operation should not cause the device to lose the status of the timer nor the count of events. Rationale - permitting a Step Upthrust Device to automatically reset one time within 24 hours of operation lowers the minimum safety standard. The ability for an electromechanical machine to effectively rule out a hazardous condition being present as opposed to elevator personnel ruling out the presence of a hazard has not been proven to ensure safety to the riding public. | Reference Scott Hultstrom written comments in Public Testimony NEII COMMENTS: See comments regarding the previous Public Input on 6.1.6.3.6. ASME has determined the current code language offers enhanced safety when compared to the option of permitting the general public to use the non-operating escalator as a stairway until qualified personnel can arrive to reset the escalator.
Scott Hultstrom | 11/12/19 Public Comments and Submitted Written Comments | 6.1.6.3.12 | 6.1.6.3.12 Handrail Entry Device revise as follows: A handrail entry device shall be provided at each newel. It shall be operative in the newels in which the handrail enters the balustrade. It shall cause the escalator to stop by removing power from the driving-machine motor and brake. It shall operate in either of two ways:(a)if an object becomes caught between the handrail and the handrail guard(b) if an object approaches the area between the handrail and handrail guard for those units that rely on an opening of the balustrade to prevent entrapment, all handrail entry devices shall be operative whenever the handrails are operating. The device shall be of the manual reset type REMOVE THE FOLLOWING LANGUAGE: or it shall be permitted to automatically reset not more than one time within 24 hr of operation and thereafter require a manual reset before the next restmt. Interuption of power during operation should not cause the device to lose the status of the timer nor the count of events. Rational - Permitting a Handrail Entry Device to automatically reset one time within 24 hour of operation lowers the minimum safety standard. The ability for an electromechanical machine to effectively rule out a hazardous condition being present as opposed to elevator personnel ruling out the presence of a hazard has not been proven to ensure safety to the riding public. | Reference Scott Hultstrom written comments in Public Testimony NEII COMMENTS: External examination of the handrail entry device (6.1.6.3.12) and handrail speed-monitoring device (6.1.6.4) can be performed by a visual check. Therefore, the manual reset requirements were removed to permit self-resetting provided not more than one activation occurs in a 24-h period of operation for either of these protective devices. ASME has determined the current code language offers enhanced safety when compared to the option of permitting the general public to use the non-operating escalator as a stairway until qualified personnel can arrive to reset the escalator.
Scott Hultstrom | 11/12/19 Public Comments and Submitted Written Comments | 6.1.6.4 | A handrail speed monitoring device shall be provided that will cause the activation of the alarm required by 6 .1. 6 .3 .1 (b) without any intentional delay, whenever the speed of either handrail deviates from the step speed by 15% or more. The device shall also cause electric power to be removed from the driving-machine motor and brake when the speed deviation of 15% or more is continuous within a 2 s to 6 s range. The device shall be of the manual reset type REMOVE THE FOLLOWING LANGUAGE: or it shall be permitted to automatically reset not more than one time vlithin 24 hr of operation and thereafter require a manual reset before the next restart. Interruption of power during operation should not cause the device to lose the status of the timer nor the count of events. Rationale - Permitting a Handrail Speed Monitoring Device to automatically reset one time within 24 hour of operation lowers the minimum safety standard. The ability for an electromechanical machine to effectively rule out a hazardous condition being present as opposed to elevator personnel ruling out the presence of a hazard has not been proven to ensure safety to the riding public. | Reference Scott Hultstrom written comments in Public Testimony NEII COMMENTS: External examination of the handrail entry device (6.1.6.3.12) and handrail speed-monitoring device (6.1.6.4) can be performed by a visual check. Therefore, the manual reset requirements were removed to permit self-resetting provided not more than one activation occurs in a 24-h period of operation for either of these protective devices. ASME has determined the current code language offers enhanced safety when compared to the option of permitting the general public to use the non-operating escalator as a stairway until qualified personnel can arrive to reset the escalator.
Scott Hultstrom | 11/12/19 Public Comments and Submitted Written Comments | 6.2.6.3.10 | 6.2.6.3 .10 Handrail Entry Device revise as follows A handrail entry device shall be provided at each newel. It shall be operative in the newels in which the handrail enters the balustrade. It shall cause the moving walk to stop by removing power from the driving-machine motor and brake. It shall operate in either of two ways (a) if an object becomes caught between the handrail and the handrail guard (b) if an object approaches the area between the handrail and handrail guard for those units that rely on an opening of the balustrade to prevent entrapment, all handrail entry devices shall be operative whenever the handrails are operating. The device shall be of the manual reset type REMOVE THE FOLLOWING LANGUAGE: or it shall be permitted to automatically reset not more than one time within 24 hr of operation and thereafter require a manual reset before the next restart. Interuption of power during operation should not cause the device to lose the status of the timer nor the count of events. Rationale - Permitting a Handrail Entry Device to automatically reset one time within 24 hours of operation lowers the minimum safety standard. The ability for an electromechanical machine to effectively rule out a hazardous condition being present as opposed to elevator personnel ruling out the presence of a hazard has not been proven to ensure safety to the riding public. | Reference Scott Hultstrom written comments in Public Testimony NEII COMMENTS: External examination of the handrail entry device (6.1.6.3.12) and handrail speed-monitoring device (6.1.6.4) can be performed by a visual check. Therefore, the manual reset requirements were removed to permit self-resetting provided not more than one activation occurs in a 24-h period of operation for either of these protective devices. ASME has determined the current code language offers enhanced safety when compared to the option of permitting the general public to use the non-operating escalator as a stairway until qualified personnel can arrive to reset the escalator.
Scott Hultstrom | 11/12/19 Public Comments and Submitted Written Comments | 6.2.6.4 | 6.2.6.4 Handrail Speed Monitoring Device revise as follows A Handrail Speed Monitoring Device shall be provided that will cause the activation of the alarm required by 6.2.6.3.l(b) without any intentional delay whenever the speed of either handrail deviates from the treadway speed by 15% or more. The device shall also cause electric power to be removed from the driving-machine motor and brake when the speed deviation of 15% or more is continuous within a 2 s to 6 s range. The device shall be of the manual reset type REMOVE THE FOLLOWING LANGUAGE: or it shall be permitted to automatically reset not more than one time within 24 hr of operation and thereafter require a manual reset before the next restart. Interruption of power during operation should not cause the device to lose the status of the timer nor the count of events. Rationale - permitting a Handrail Speed Monitoring Device to automatically reset one time within 24 hours of operation lowers the minimum safety standard. The ability for an electromechanical machine to effectively rule out a hazardous condition being present as opposed to elevator personnel ruling out the presence of a hazard has not been proven to ensure safety to the riding public. | Reference Scott Hultstrom written comments in Public Testimony NEII COMMENTS: External examination of the handrail entry device (6.1.6.3.12) and handrail speed-monitoring device (6.1.6.4) can be performed by a visual check. Therefore, the manual reset requirements were removed to permit self-resetting provided not more than one activation occurs in a 24-h period of operation for either of these protective devices. ASME has determined the current code language offers enhanced safety when compared to the option of permitting the general public to use the non-operating escalator as a stairway until qualified personnel can arrive to reset the moving walk.
Scott Hultstrom | 11/12/19 Public Comments and Submitted Written Comments | 6.1.2.3 | 6.1.2.3 (add 3) Add as this was never an ASME approved deletion ADD THE FOLLOWING LANGUAGE: Where a defective part directly affecting the safety of the operation is identified, the equipment shall be taken out of service until the defective part has been adjusted, repaired, or replaced. Rationale - This was omitted during ASMF, processes of developing standards. No code making body is above a mistake. Add this as there are hundreds of defective products that have been identified with little or no knowledge as to this fact. | Reference Scott Hultstrom written comments in Public Testimony NEII COMMENTS: The ASME Editorial Committee has recommended an Errata to reinsert this requirement into the code.
Scott Hultstrom | 11/12/19 Public Comments and Submitted Written Comments | 2.12.7.3.3(c) | 2.12.7.3.3(c) revise as follows REMOVE THE FOLLOWING LANGUAGE: If the lowest landing is the normal means of access to the pit, the hoistway access switch shall enable the car to move in the up direction to a point between 2 13 0 mm (84 in.) and 2 450 mm (96 in.) from the floor level to the bottom of the platform guard, unless the travel of the car limits such movement. ADD THE FOLLOWING LANGUAGE: The movement of the car initiated and maintained by the hoistway access switch at the lowest landing, if this landing is the normal means of access to the pit, shall be limited in the up direction to the point where the bottom of the platform guard is even with hoistway entrance header. Rationale - The advent of new technology has made it difficult to impossible to control an elevator using a PM drive motor. A safety code should not negate safe language limiting car travel because the new technology has reduced effective control of the machinery. | Reference Scott Hultstrom written comments in Public Testimony NEII COMMENTS: The code requirement has nothing to do with car control or PM drive motors. This requirement ensures that the hoistway access switch can raise the car high enough for elevator personnel to safely access and egress the pit unless the car is incapable of traveling to such an elevation, e.g., a very short hoistway. The 12 inch window provides a tolerance. In some cases, the total travel of the elevator is less than 84 inches. Since the access switch cannot move the elevator beyond the distance it is able to travel, the exception is needed for these limited applications.
Scott Hultstrom | 11/12/19 Public Comments and Submitted Written Comments | 6.1.7.4.3 and 6.2.7.4.3 | 6.1.7.4.3 and 6.2.7.4.3 reference a standard that does not derive its language from safety, is not a safety standard and specifically does not address a safety circuit being affected by various devices transmitting wirelessly. Please assemble your AHJ to re-evaluate this referenced standard. Rationale: As a member of an ISO committee I have been out voted and instructed that ISO standards are not safety standards, but rather marketing standards designed to increase business globally. | Reference Scott Hultstrom written comments in Public Testimony NEII COMMENTS: The ISO 22200 Standard is an international standard that provides safety requirements for electromagnetic interference testing for escalator and moving walk control circuits instead of the previous European standard. It is not a marketing standard. This is consistent with requirements for elevator controls (see 2.26.4.4). This standard is recognized internationally, and no justification is provided as to why this provision is of concern or should be modified/removed as opposed to the single requirement currently in A17.1/B44. Contrary to the public comment, ISO 22200 is a safety standard as noted in the following Abstract from the ISO website: “ISO 22200:2008 specifies the immunity performance criteria and test levels for apparatus used in lifts, escalators and moving walks which are intended to be permanently installed in buildings, including the basic safety requirements regarding their electromagnetic compatibility (EMC) environment. These levels represent essential EMC requirements. ISO 22200:2008 refers to normal EMC conditions as existing in residential, office and industrial buildings.” The test frequencies as required within the ISO 22200 standard are within the same frequencies required to be tested as part of the FCC Part 15 for generic product certification.
Scott Hultstrom | 11/12/19 Public Comments and Submitted Written Comments | 3.24.5 | Please prohibit a hydraulic machine to be located in a hoistway/pit. ADD THE FOLLOWING LANGUAGE: 3.24.5 Location of Tanks Hydraulic machines being installed in the line of movement of an elevator car or wherein an affected person is required to work in the line of movement of an elevator car shall be prohibited. Rationale: April of 2018 an affected person was killed by an engineered hazard which never was compliant with published standards. Due to this fatality increased local enforcement to prevent further fatalities is warranted. | Reference Scott Hultstrom written comments in Public Testimony NEII COMMENTS: Section 3.4 within A17.1 provides the appropriate clearance requirements for equipment located within the elevator pit under the elevator car. A17.1 has assigned an ad-hoc safety committee (diverse group of the current ASME A17.1 members) to review various industry incidents and, if any enhancements to A17.1 are identified, improved safety will be addressed by the appropriate sub-committees.
Scott Hultstrom | 11/12/19 Public Comments and Submitted Written Comments | Process | I have provided a rough list you can use to evaluate the adoption of multiple standards thus empowering you, The AHJ to carefully and responsibly move forward as you wish. Please remember that jurisdictions such as California enforce an older edition of the applicable standards yet have a more advanced variance process allowing safe enforcement. Please consider stepping back and evaluating how you move forward with your adoption. If any support is desired, we are willing to assist as needed. | Reference Scott Hultstrom written comments in Public Testimony NEII COMMENTS: Jurisdictions that delay regularly reviewing and updating their elevator code are adding significant subjective criteria to allowing the installation of equipment into a jurisdiction. A subjective reviewal process for installing widely used, code complaint equipment is unnecessarily burdensome for owners and manufactures without demonstrably safer results. There is no evidence that an advanced variance process is a better mechanism for safe enforcement than regularly updating the code. In fact, the opposite has been borne out in practice. Close to 75% of states, including neighboring Maryland, New Jersey, New York, and Ohio have adopted one of the two most recently published code editions. Even California, referenced in the comment above, is set to undertake an update of their code to reflect a more recent iteration of the model standard.
Scott Hultstrom | 11/12/19 Public Comments and Submitted Written Comments | Process | Please consider assembling your safety board or committee, and if that board or committee does not exist assemble an ad hoc board to, recognize, communicate and ultimately adopt codes and standards only after a comprehensive review of the language. Rationale: In an attempt to assure the provision of professional services is enabling the most efficient and effective use of the state's public safety resources, allowing for the consolidation of such functions as communications, training, and operating procedures and to protect the lives and promote the safety of the citizens of this state. It is essential to the maintenance of a democratic society that language being proposed undergoes due diligence vetting its possible effect on the citizens of your communities. The changes in ASME Al 7.1/CSA B44 as each edition is published are radically different from any previous edition and you are embarking on a journey to adopt at least 1600 changes. You are not prepared to do this responsibly from my vantage point. There are people present in this room who claim complete and comprehensive knowledge of the safe adoption of this 2016 edition. I am a highly skilled elevator constructor in the areas of safety, standards, fundamental process development and would never make any claim to understand adopting a new standard without looking at each subsequent edition coming after that which I have accepted so as to safeguard those in my charge. I ask anyone hearing these words to ask themselves if they would stand before the men, women, children and all they are sworn to protect and promise they understand that which they are adopting. | Reference Scott Hultstrom written comments in Public Testimony NEII COMMENT on the process ... Without careful consideration of the unintended consequences of changing A17.1, it is ill-advised to adopt significant modifications. While it is not uncommon for jurisdictions around the country to make minor modifications to conform the elevator code with local circumstances, the reason that no more than ten jurisdictions make significant changes is because they trust ASME’s rigorous consensus balloting system, overseen by a balanced committee of industry experts. Local changes to the model code should be dictated by conditions completely unique to a jurisdiction such as extreme weather, seismic threats, and alignment with local administrative laws. Local changes should not be dictated by politics or baseless claims. Root causes of incidents need to be examined and empirical data should be offered to justify making any deviations to the code. See written comments, dated 12/16/19 for full text
Dennis Bartnick | 11/12/19 Public Comments | Process | This is not a one-size­ fits all world, you can't just walk in and adopt the whole thing, "Let's take it all." You can't. | Note: No submitted written testimony
Ed Loomis | 11/12/19 Public Comments and Submitted Written Comments | Multiple, see in text to right | Alternative testing claims their methods reduce the possibility of injury to personnel. We have yet to see any report of this claim. If qualified personnel perform an actual test with weights, deficiencies will be revealed and addressed...Alternative predictive does not use a practice of randomly placing actual test weights in a car enclosure. Alternative testing not using this does not valuate how a car sits, rides during the test, decelerates, stops and holds the elvator. Unless additional requirements are developed alternative testing cannot replace actual weight testing...For this reason at some point I respectfully ask that you undertake an action item to require weighing of elevator systems using an analog means...This will not only increase safety but decrease costs to building owners and elevator companies. Our industry can be expensive. As long as safety prevails the financial burden should be eased when possible to our building owners. Please delete the following in ASME. A17.1-2016/CSA B44-16: 1. 6.4.20.l(b) 2. References to 8.6.11.10 in 8.6.4.20.3(-a) 3.References to 8.6.11.10 in 8.6.4.20.3(-b) 4.References to·8.6.11.10.in 8.6.4.20.3(f) 5.8.6.4.20.4(b)6.8.6.4.20.l0(b) 7.8.6.11.10 and its subordinate requirements 8.The note referencing 8.6.11.10 in the parent paragraph in Section 8.10 | See Ed Loomis written comments in public testimony for additional information
Elizabeth Baldwin | Written Comments only, received 11/12/19 | None stated | The Departmentof Licenses and Inspections supports the adoption of ASME Al 7.1 2016 and recommends that regulations be expanded to include relevant accessibility provisions of the International Building Ccide and ICC A 117.1 . The current regulation requires a separate review, permit, and inspection by the local jurisdiction to confim that the elevator or lifting device meets accessibility provisions. We recommend that the Department of Labor and Industry incorporate accessibility provisions that address dimensions and controls into the permitting process. A single authority will streamline the process, shorten the overall review time, and eliminate the duplication of work. | Reference Elizabeth Baldwin Written Testimony in public testimony
Elizabeth Baldwin | Written Comments only, received 11/12/19 | None stated | I am also here to share comment from the Mayor's Office. The Mayor's Office of Labor Relations is not supportive of the alternate testing method proposed in the new code. Alternative testing is not actual testing. The manufacturers want to use alternative methods of testing that predict the results. Alternative predictive testing could increase the dangers to the riding public as elevators would be tested without using real life conditions (i.e. test weights). | Reference Elizabeth Baldwin Written Testimony in public testimony
Jim Chapman | Written Comments only, received 11/12/19 | ASME A17.1-2016/CSA B44-16. | I would like to express my concerns about altern􀀏tive testing that is in ASME A17.1-2016/CSA B44-16. We have always done testing using straight forward methods and always used qualified personnel. Our goal is to follow these methods and eliminate hazards to the riding public. Those who sell alternative testing technology require a baseline during the final acceptance test using weights. There are no requirements in A17.1 to use weights to set the baseline, only a note. Notes are not requirements and can't be enforced... I respectfully request that the Pennsylvania Elevator Safety Board delete the following in ASME A17.1-2016/CSA B44-16: • 8.6.4.20. l{b) • References to 8.6.11.10 in 8.6.4.20.3{-a) • References to 8.6.11.10 in 8.6.4.20.3{b) • References to 8.6.11.10 in 8.6.4.20.3{f) • 8.6.4.20.4{b) • 8.6.4.20.l0{b) • 8.6.11.10 and its subordinate requirements • The note referencing 8.6.11.10 in the parent paragraph in Section 8.10 | See Jim Chapman Written Testimony in public testimony for additional details NEII COMMENTS: Alternative testing was added in the 2013 edition of ASME after passing a rigorous, consensus process. The code recognizes that certain technology exists that allows safety tests to be performed without the need for elevator personnel to move heavy weights, thereby reducing the likelihood of injury to elevator personnel. Strains and sprains, which are often the direct result of moving the thousands of pounds of weights required for these tests, account for over half of all injuries to elevator personnel. Additionally, the Department retains the ability to authorize any alternative testing before it’s implemented in the Commonwealth. Requirement 8.6.11.10.3.6(c) requires correlation with “previously acquired full-load and no load results” meaning that the baseline has to be conducted with full-load.
Dylan Isenberg/NEI | Written Comments dated 12/16/19 | None Stated | Power Shut Off location for MRLs It seems there is no identified required location for the main drive power shut off switch (not an upstream breaker or feed as this does not guarantee removal of potential energy from back-up battery or other sources, if installed). I have found them installed in obscure, remote locations that would not be anticipated, I have found them on various floors within the same building, and I frequently find them installed in the elevator door bucks (door jamb) near the entrance point, inside a locked cabinet. For a long period of time, the FD only had to catalog keys for the machine room door lock, hoist way door keys, and fire service control keys. It is paramount for safety reasons, that the main drive power be shut off, and the only acceptable location is the designed power control point for the elevator machine (drive system), not an upstream breaker or switch. The control point was found in the machine room, whether hydraulic drive or cabled-traction overhead machine room. With MRL's we have no idea where it may be. It appears, but I am uncertain, that code does not require a standard location for power control points for MRL's. / am unsure of the fix, but the FD needs to know the location of the power control point, and also needs access to locked areas to control power before beginning non-destructive techniques described in ASME A17.4. I am finding that the key to the power control points inside locked cabinets are keys other than the fire service.control key. My recommendation is that wherever MRL's are installed, the location of the designed power control point for the drive machine, be communicated to the FD along with identification of any required keys to access this power control point. NEII COMMENTS: Location of the main line disconnect in addition to disconnecting of battery lower devices within A17.1 references NFPA-70(NEC), which is covered in very explicit detail within article 620.51. A17.1 inquiry 16-3025 in fact addresses the additional contact requirement to detect the removal of power to prohibit movement on battery power. MRLs are required to provide information for the location of the disconnects as per the National Electric Code. Manufactures and provide this information on their power data layout drawings. Also, note that local fire departments have information regarding the location of these disconnects and associated safety equipment by standard operating procedures

## Board Mtg and Q & A, need codes
Suggested By | Date of Suggestion | Code Reference | Suggestion | Notes
Mr Loomis | 2019-08-19 |  | Should not allow alternative testing, and should not allow variances to do this testing. | Public Comment
All Board, Mr Sims | 2019-03-07 |  | Single access fire key for all PA elevators. | Motion made and approved to send to Secretary
Mr. Wade | 2019-10-18 | A17.3 | eliminate single bottom jacks in a three year time frame. | Motion made and passed to eliminate single bottom jacks in a three year time frame.
Ms. Sieber | 2019-10-18 |  |  | Motion to submit recommendation to the Secretary to pursue legislative action regulating elevators in private residences.
MR. GIELAROWSKI, MR. CLARK, MR. SCOTT and MR. SIMS | 11.12.19 | None stated | After Mr. Clarks public testomony, Mr. Geilarowski asked what Mr. Clark thought about sprinklers in machine rooms. Lenthy discussion ensued. Mr. Clark said, I just think the shunt trips, if they're installed, can be a problem for firefighters on serious fires. Mr. Geilarowski said the fire chief in Pittsburgh has no problem with them removing them. Additional discussion on this ensued. | Reference page 39 -44 of 11.12.19 Public testimony document
MR. GIELAROWSKI and MR. CLARK | 11.12.19 | None stated | Discussion about required fire testing and whose responsibility it is to ensure this gets completed timely | Reference page 49-51 of 11.12.19 Public testimony document
MR. SIMS AND MR. WALSH | 11.12.19 | None stated | Discussion about the need for a defined closet with a door that can be closed to protect the mechanic working on the escalator | Reference page 65 & 66 of 11.12.19 Public testimony document
MR. SIMS AND MR. KOCH | 11.12.19 | None stated | Discussion about requiring a rope gripper | Reference page 81-82 of 11.12.19 Public Testimony document
MR. KOCH, MS. SIEBER, MR. WILLIAMS, MR. GIELAROWSKI AND MR. SIMS | 11.12.19 | None stated | Discussion about requiring a working platform | Reference page 83-86 of 11.12.19 Public Testimony document
MR. HULSTROM | 11.12.19 | None stated | Discussion about private residences and the fact they should also have safeguards in place | Reference page 118-120 of 11.12.19 Public Testimony document
MR. HULSTROM | 11.12.19 | None stated | I urge you to codify and adopt ASME's Al7.8 wind turbine standard | Reference page 120 of 11.12.19 Public Testimony document
MR. HULSTROM | 11.12.19 | None stated | Discussion about alternative testimony and making people test weights | Reference page 121 of 11.12.19 Public Testimony document
MR. HULSTROM | 11.12.19 | None stated | Discussion about TIP's and MCP's | Reference page 124-128 of Public Testimony document
Board Members | 9.17.19 | None stated | Discussion about recommending to the secretary to eliminate single bottom jacks and give a 3 year time frame for complete replacement. Motion carried. | Reference page 88-98 of 9.17.19 Elevator Board Minutes
Board Members | 9.17.19 | None stated | Discussion about recommending to the secretary that there be consideration of legislative action to require inspecations of residential elevators. Motion carried. | Reference page 98-103 of 9.17.19 Elevator Board Minutes
Norman Martin, Schindler Elevator | 9.17.19 | None stated | Adopt A-17.3 specifically and your standards that you've outlined under your new proposal, or under 405.2, as well as ensuring that A-17.6 regarding suspension standards is part of that reference | Reference page 105-108 of 9.17.19 Elevator Board Minutes
MR. SIMS AND MR. SCOTT | 10.17.19 | None stated | Single bottom cylinder issue should be lifted out and put forward because it’s a safety issue | Reference page 53- 54 of the 10.17.19 Elevator Board Minutes
MR. WILLIAMS, MR. MARCHIONI, MR. WADE, MS. MANGANELLO, MR. WEIANT, MR. HULSTROM, MR. VON GETZIE, MR. ISENBERG | 10.17.19 | None stated | Discussion about A-17.3 and how to handle it, during the reg process or seperately | Reference page 55- 72 of the 10.17.19 Elevator Board Minutes
MR. SIMMS | 11.19.19 | None stated | The new code should address the mounting system and the way were going to accept that in the future and the reason why is the thrusts and loads that are being enforced onto the rails can crush the drywall and its only a wood lagging system that lag bolts into wood and over a long period of time, it could loosen up | Reference page 10 of the 11.19.19 Elevator Board Minutes
MR. WILLIAMS AND MR. SIMMS | 11.19.19 | None stated | In the new code, the board needs to get a reason why they are asking for a limited use, limited access elevator as opposed to a commercial elevator. | Reference page 13 of the 11.19.19 Elevator Board Minutes
MR SIMMS | 11.19.19 | None stated | In the new code, we may actually be redfining elevator personnel | Reference page 29 of the 11.19.19 Elevator Board Minutes
MS. BERRIER, MR. WADE, MR. SIMMS, MS. SIEBER | 11.19.19 | None stated | During discussion about including home elevators in inspections, Mr. Wade states that we believe existing elevators should be corrected too.

## Elevator Division
Suggested By | Date of Suggestion | Code Reference | Suggestion | Notes
Elevator Division | 2019-08-19 | UCC 401.1 Definitions | Add definition to 401.1 Elevator Personnel: Persons who are enrolled in or have completed a certified apprentice program approved by the Commonwealth of Pennsylvania. (replace definition of Elevator Personnel with definition listed in 401.1) | A17.1-2016 - levator personnel: persons who have been trained in the construction, maintenance, repair, inspection, or testing of equipment. See Document ER-1
Elevator Division | 2019-08-16 | A17.1-2016 21 2.2.4.2 | Remove language permitting retractable ladders. Retractable ladders lead to less clearance in shaft, increasing the risk of caught between, struck by hazards. | A17.1-2016 21 2.2.4.2 The ladder is permitted to be retractable, shall conform to 2.2.4.2.1 through 2.2.4.2.3 and 2.2.4.2.5 through 2.2.4.2.8. When in the extended position, retractable ladders shall conform to 2.2.4.2.4. Retractable ladders must meet the same requirements of a fixed ladder See Document ER-2
Elevator Division | 2019-08-17 | A17.1-2016 32 2.7.5.4 & A17.1-2016 21 2.7.5.3 | Why would we allow a working platform to be installed in the line of movement of the car or counterweight? Working platforms in the line of movement of the car or counterweight. | Working platforms. A platform located in the car, on the car, or in the hoistway shall be permitted for access to an maintenance and inspection of equipment in machinery spaces or control spaces in the hoistway and shall comply with 2.7.5.3.1 through 2.7.5.3.6 (see also 8.6.11.8). See Document ER-3
Elevator Division | 2019-08-18 | A17.1-2016, A17.1-2016, | AGP, Accessibile to general public is not defined in the standards definitions. AGP needs to be clearly defined. A sign inside the controller door is not effective. In an area that the code is stating is accessible to the general public the sign needs to be placed in a position that the general public can see and understand. Replace the language pertaining to the sign to read: shall be prominently posted on the outside of the of motor controller closet/room door indicating in letters not less than 25 mm (1 in) high, CAUTION ENSURE AREA IS SECURED AND SAFE BEFORE OPENING. | Labeled/marked "AGP" in accordance with the requirements of CSA B44.1/ASME A17.5 (see 2.26.4.2). 32-33 2.7.6.3.2(f) provided with a sign in conformance with the requirements of ANSI Z535.2 or CAN/CSA-Z321, that shall be prominently posted on the inside of the motor controller cabinet door indicating in letters not less than 25 mm (1 in.) high, "DOOR TO BE CLOSED AND LOCKED WHEN ELEVATOR PERSONNEL ARE NOT PRESENT AT THIS CONTROLLER." See Document ER-4
Elevator Division | 2019-08-16 | A17.1-2016 2.12.7.2.1, & A17.1-2016 2.12.7.2.2 | Hoistway Access Switch - Sight Guard, | Remove (c) installing an access switch on a sight guard is creating more struck by, caught between and electrocution hazards by moving personnel closer to moving parts. A17.1-2016 2.12.7.2.2 Remove along with (c) from 2.12.7.2.1 See Document ER-5